{"text_format":"1","workbook":"xlsx","n_sheets":2,"sheets":["負荷原単位","想定負荷"],"not_rendered":{"charts":4,"images":4,"macros":1,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"負荷原単位","index":0,"n_rows":105,"n_cols":38,"rows_kept":105,"cut":false,"hidden":false,"merged":[[4,9,4,10],[4,11,4,12],[21,3,21,4],[21,6,21,8]]}
[null,"１．熱負荷の想定"]
[null,null,null,null,null,null,"：入力データ",null,null,null,null,null,null,null,null,null,null,null,null,null,"（参考資料）"]
[null,"（１）建物概要",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"■熱負荷原単位",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"■全負荷相当運転時間"]
[null,null,null,null,null,null,null,"☆地域No.と地域係数表"]
[null,"地域No.",4,null,null,null,null,"地域No.","地域","最大熱負荷",null,"年間熱負荷"]
[null,null,null,null,null,null,null,null,null,"冷房","暖房","冷房","暖房"]
[null,null,null,null,null,null,null,1,"北海道",0.8,1.5,0.5,2.4]
[null,"建物用途",null,"延床面積","稼働率",null,null,2,"東北",0.9,1.3,0.7,1.4]
[null,null,null,"m2","註１）",null,null,3,"北陸",1,1.1000000000000001,0.9,1.4]
[null,"業務施設",null,20000,1,null,null,4,"関東",1,1,1,1]
[null,"宿泊施設",null,null,null,null,null,5,"東海",1,1,1.1000000000000001,0.9]
[null,"商業施設",null,null,null,null,null,6,"近畿",1,1,1.1000000000000001,0.9]
[null,"医療施設",null,null,null,null,null,7,"中国",1,1,1.1000000000000001,0.9]
[null,"集合住宅",null,null,null,null,null,8,"四国",1,1,1.1000000000000001,0.9]
[null,null,null,null,null,null,null,9,"九州",1,1,1.2,0.7]
[null,"合計",null,{"$f":"SUM(D10:D15)","v":20000},"－",null,null,10,"沖縄",1.1000000000000001,0.5,1.5,7.0000000000000007E-2]
[null,"註１）稼働率を乗じて計算する。(通常は1.0)",null,null,null,null,null,"出典）低炭素まちづくり実践ハンドブック　国土交通省"]
[null,null,null,null,null,null,null,"註）負荷原単位に地域係数を乗じて計算する。"]
[]
[null,"（２）負荷原単位"]
[]
[null,null,null,"ﾋﾟ-ｸ負荷(W/m2)",null,"全負荷相当","年間負荷(単位/年)",null,null,"出典"]
[null,null,null,"設計値","×稼働率","時間 h","設計値","×稼働率","単位"]
[null,null,"電力",53,{"$f":"D24*$E$10","v":53},{"$f":"IF(E24=0,0,H24/E24*1000)","v":2943.3962264150941},156,{"$f":"G24*$E$10","v":156},"kWh/m2"]
[null,"業務施設","冷房",117,{"$f":"D25*$E$10","v":117},{"$f":"IF(E25=0,0,H25/E25*1000/3.6)","v":695.63152896486235},293,{"$f":"G25*$E$10","v":293},"MJ/m2","cgs"]
[null,null,"暖房",70,{"$f":"D26*$E$10","v":70},{"$f":"IF(E26=0,0,H26/E26*1000/3.6)","v":515.8730158730159},130,{"$f":"G26*$E$10","v":130},"MJ/m2"]
[null,null,"給湯",4.8,{"$f":"D27*$E$10","v":4.8},{"$f":"IF(E27=0,0,H27/E27*1000/3.6)","v":543.98148148148152},9.4,{"$f":"G27*$E$10","v":9.4},"MJ/m2"]
[null,null,"電力",50,{"$f":"D28*$E$11","v":0},{"$f":"IF(E28=0,0,H28/E28*1000)","v":0},200,{"$f":"G28*E11","v":0},"kWh/m2"]
[null,"宿泊施設","冷房",87,{"$f":"D29*$E$11","v":0},{"$f":"IF(E29=0,0,H29/E29*1000/3.6)","v":0},419,{"$f":"G29*E11","v":0},"MJ/m2","cgs"]
[null,null,"暖房",78,{"$f":"D30*$E$11","v":0},{"$f":"IF(E30=0,0,H30/E30*1000/3.6)","v":0},335,{"$f":"G30*E11","v":0},"MJ/m2"]
[null,null,"給湯",50,{"$f":"D31*$E$11","v":0},{"$f":"IF(E31=0,0,H31/E31*1000/3.6)","v":0},335,{"$f":"G31*E11","v":0},"MJ/m2"]
[null,null,"電力",80,{"$f":"D32*$E$12","v":0},{"$f":"IF(E32=0,0,H32/E32*1000)","v":0},226,{"$f":"G32*$E$12","v":0},"kWh/m2",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"出典) 地域冷暖房技術手引書 p.335より抜粋"]
[null,"商業施設","冷房",140,{"$f":"D33*$E$12","v":0},{"$f":"IF(E33=0,0,H33/E33*1000/3.6)","v":0},523,{"$f":"G33*$E$12","v":0},"MJ/m2","cgs"]
[null,null,"暖房",93,{"$f":"D34*$E$12","v":0},{"$f":"IF(E34=0,0,H34/E34*1000/3.6)","v":0},147,{"$f":"G34*$E$12","v":0},"MJ/m2"]
[null,null,"給湯",23,{"$f":"D35*$E$12","v":0},{"$f":"IF(E35=0,0,H35/E35*1000/3.6)","v":0},96,{"$f":"G35*$E$12","v":0},"MJ/m2"]
[null,null,"電力",50,{"$f":"D36*$E$13","v":0},{"$f":"IF(E36=0,0,H36/E36*1000)","v":0},170,{"$f":"G36*$E$13","v":0},"kWh/m2"]
[null,"医療施設","冷房",105,{"$f":"D37*$E$13","v":0},{"$f":"IF(E37=0,0,H37/E37*1000/3.6)","v":0},335,{"$f":"G37*$E$13","v":0},"MJ/m2","cgs"]
[null,null,"暖房",105,{"$f":"D38*$E$13","v":0},{"$f":"IF(E38=0,0,H38/E38*1000/3.6)","v":0},310,{"$f":"G38*$E$13","v":0},"MJ/m2"]
[null,null,"給湯",47,{"$f":"D39*$E$13","v":0},{"$f":"IF(E39=0,0,H39/E39*1000/3.6)","v":0},335,{"$f":"G39*$E$13","v":0},"MJ/m2"]
[null,null,"電力",30,{"$f":"D40*$E$14","v":0},{"$f":"IF(E40=0,0,H40/E40*1000)","v":0},50,{"$f":"G40*$E$14","v":0},"kWh/m2"]
[null,"集合住宅","冷房",47,{"$f":"D41*$E$14","v":0},{"$f":"IF(E41=0,0,H41/E41*1000/3.6)","v":0},33,{"$f":"G41*$E$14","v":0},"MJ/m2","cgs"]
[null,null,"暖房",35,{"$f":"D42*$E$14","v":0},{"$f":"IF(E42=0,0,H42/E42*1000/3.6)","v":0},84,{"$f":"G42*$E$14","v":0},"MJ/m2"]
[null,null,"給湯",27,{"$f":"D43*$E$14","v":0},{"$f":"IF(E43=0,0,H43/E43*1000/3.6)","v":0},126,{"$f":"G43*$E$14","v":0},"MJ/m2",null,"出典）","cgs","都市ガスによるコージェネレーションシステム計画・設計と評価　（公社）空気調和・衛生工学会"]
[null,null,"電力",null,{"$f":"D44*$E$15","v":0},{"$f":"IF(E44=0,0,H44/E44*1000)","v":0},null,{"$f":"G44*$E$15","v":0},"kWh/m2",null,null,"dhc","地域冷暖房技術手引書　（一社）都市環境エネルギー協会"]
[null,null,"冷房",null,{"$f":"D45*$E$15","v":0},{"$f":"IF(E45=0,0,H45/E45*1000/3.6)","v":0},null,{"$f":"G45*$E$15","v":0},"MJ/m2",null,null,null,"to","東京都平均"]
[null,null,"暖房",null,{"$f":"D46*$E$15","v":0},{"$f":"IF(E46=0,0,H46/E46*1000/3.6)","v":0},null,{"$f":"G46*$E$15","v":0},"MJ/m2",null,null,null,"ku","空衛学会"]
[null,null,"給湯",null,{"$f":"D47*$E$15","v":0},{"$f":"IF(E47=0,0,H47/E47*1000/3.6)","v":0},null,{"$f":"G47*$E$15","v":0},"MJ/m2",null,null,"decc","建物用途別負荷原単位及び未利用エネルギーデータの整備　空気調和・衛生工学会論文集 No.239, 2017年2月 より作成."]
[null,"註）赤字の負荷原単位：　全負荷相当時間等を考慮し調整した。",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"出典）空気調和・衛生工学便覧第14版　３空気調和設備設計編 p.319より抜粋"]
[]
[]
[]
[null,"（３）負荷パタ－ン"]
[]
[null,"１）月別負荷パタ－ン"]
[]
[null,"月",null,null,"業務施設",null,null,null,null,"宿泊施設",null,null,null,null,"商業施設",null,null,null,null,"医療施設",null,null,null,null,"集合住宅"]
[null,null,"日数","電力","冷房","暖房","給湯","日数","電力","冷房","暖房","給湯","日数","電力","冷房","暖房","給湯","日数","電力","冷房","暖房","給湯","日数","電力","冷房","暖房","給湯","日数","電力","冷房","暖房","給湯"]
[null,1,23,7.15,0,26.263871763255242,6.6666666666666652,24,8.1218274111675139,0.8,20.57,10.14,27,7.11,1.2,32.799999999999997,7.66,23,7.94,1.5006252605252188,27.49,9.51,22,10.029999999999999,0,24.06,12.1,31]
[null,{"$f":"B58+1","v":2},23,7.43,0,22.811344019728732,6.6666666666666652,21,7.6706147772137623,0.8,17.87,10.07,24,7.11,1.5,29.64,8.02,22,7.41,1.3755731554814505,21.2,9.98,19,8.6300000000000008,0,20.03,10.8,28]
[null,3,25,8.15,0,18.7422934648582,13.33333333333333,24,7.8962210941906381,1,14.41,9.51,27,7.67,2.1,15.87,9.17,24,8.11,1.7924135056273445,19.920000000000002,10.050000000000001,21,8.8699999999999992,0,20.079999999999998,9.9,31]
[null,4,24,7.9,0,9.0012330456226888,15.999999999999998,23,8.009024252679076,3.2,12.48,8.65,26,7.9,4.3,0,9.07,23,7.64,1.7924135056273445,2.67,9.85,20,8.4700000000000006,0,8.11,10,30]
[null,5,22,8.0299999999999994,3.92,0,6.6666666666666652,24,8.2346305696559519,8.1999999999999993,3.07,7.78,27,8.9600000000000009,9.6,0,7.83,23,7.79,5.2938724468528546,0,8.09,22,7.78,0,0,8.1,31]
[null,6,25,8.9499999999999993,15.67,0,6.6666666666666652,23,8.4602368866328277,13.4,0,7.33,27,9.33,14.2,0,7.26,23,8.4499999999999993,11.588161734055856,0,7.88,20,6.86,7.96,0,6.5,30]
[null,7,26,10.07,27.63,0,6.6666666666666652,23,8.7986463620981397,20.2,0,7.33,27,9.42,15.8,0,7.99,25,9.33,21.258857857440599,0,7.13,20,8.17,32.14,0,6.1,31]
[null,8,23,9.8699999999999992,30.72,0,6.6666666666666652,24,9.0806542583192353,24.3,0,6.23,27,8.91,22.5,0,7.84,24,10.06,26.886202584410167,0,5.54,21,9.49,47.76,0,4.9000000000000004,31]
[null,9,23,8.89,19.79,0,6.6666666666666652,23,8.6858432036097035,16.5,0,7.02,27,9.4499999999999993,15.4,0,8.1199999999999992,23,8.85,18.174239266360985,0,5.76,21,8.2799999999999994,12.14,0,5,30]
[null,10,25,8.66,2.27,0,6.6666666666666652,24,8.5166384658770458,8,0,7.58,27,8.74,8.3000000000000007,0,7.62,24,8.41,6.461025427261359,0,7.88,21,7.66,0,0,6.3,31]
[null,11,23,7.22,0,7.7681874229346484,12,23,8.2346305696559519,2.5,12.77,8.7200000000000006,26,7.49,3.1,0,9.07,23,8.15,2.2509378907878284,8.65,8.19,20,7.64,0,8.9499999999999993,8.1999999999999993,30]
[null,12,24,7.68,0,15.413070283600494,5.333333333333333,24,8.2910321489001699,1.1000000000000001,18.829999999999998,9.64,27,7.91,2,21.69,10.35,24,7.86,1.6256773655689869,20.07,10.14,21,8.1199999999999992,0,18.77,12.1,31]
[null,"年間",{"$f":"SUM(C58:C69)","v":286},100,99.999999999999986,99.999999999999986,99.999999999999986,280,100.00000000000001,99.999999999999986,99.999999999999986,99.999999999999986,319,99.999999999999986,100,100,100,281,100,100,100,100.00000000000001,248,100,100,100,100,365,0,0,0,0]
[null,"出典",null,"ku","ku","decc","decc",null,"decc","to","ku","ku",null,"ku","to","ku","ku",null,"ku","decc","ku","ku",null,"ku","ku","ku","to"]
[null,"註）日数は各月代表日を算出すための仮定値。"]
[]
[]
[null,"２）時刻別負荷パタ－ン"]
[]
[null,"時刻",null,"業務施設",null,null,null,"宿泊施設",null,null,null,"商業施設",null,null,null,"医療施設",null,null,null,"集合住宅"]
[null,null,"電力","冷房","暖房","給湯","電力","冷房","暖房","給湯","電力","冷房","暖房","給湯","電力","冷房","暖房","給湯","電力","冷房","暖房","給湯","電力","冷房","暖房","給湯"]
[null,1,0.73,0,0,0,2.54,2.5,3.05,2.37,0.1,0,0,0,2.09,1.6,0.2,0.57999999999999996,1.3,0.3,4,2.7]
[null,{"$f":"B79+1","v":2},0.69,0,0,0,2.41,2.5,3.43,1.43,0.1,0,0,0,2.04,1.6,0.3,0.45,1.3,0.3,2.6,0.3]
[null,3,0.69,0,0,0,2.41,2.1,3.81,0.64,0.1,0,0,0,2,1.5,0.3,0.35,1.3,0.3,1.8,0.2]
[null,4,0.69,0,0,0,2.38,1.7,3.43,0.38,0.1,0,0,0,2.06,1.5,0.3,0.28999999999999998,0.8,0.3,1.8,0]
[null,5,0.69,0,0,0,2.5299999999999998,1.6,3.05,0.73,0.1,0,0,0,2.15,1.5,0.3,0.48,0.8,0.3,1.8,0]
[null,6,0.88,0,0,0,3.14,2.2000000000000002,3.05,2.35,0.3,0,0,0,3.02,3.4,5.0999999999999996,1.45,2.6,0.3,2.2999999999999998,0.3]
[null,7,1.86,0,0.3,1.97,3.58,2.8,3.24,4.6399999999999997,1,0,0,0,4.32,2.6,4.7,0.97,3.6,1.4,3.1,2]
[null,8,5.61,1.79,16.989999999999998,0.33,4,3.6,4.1900000000000004,4.53,6.39,7.9,0,0,5.43,2.8,4.7,0.39,4,1.9,5.6,3.5]
[null,9,7.32,9.57,12.29,1.64,4.79,4.4000000000000004,5.71,3.97,9.09,7.3,16.899999999999999,1.25,5.94,6.4,10.3,7.58,3.5,2.2999999999999998,4.4000000000000004,2.9]
[null,10,7.64,9.17,8.09,6.57,5.17,4.9000000000000004,4.95,3.8,8.89,8.3000000000000007,12.8,9.17,6.07,6.3,8.3000000000000007,9.39,3.5,2.4,4.5,3.5]
[null,11,7.66,8.9700000000000006,10.29,5.75,5.31,5.0999999999999996,5.14,4.51,8.89,8.6999999999999993,10.3,10.1,6.05,6.6,7.5,10.07,3.6,3.1,2.7,2.9]
[null,12,7.71,9.27,10.49,14.78,5.55,5.5,4.95,3.25,8.89,10,9.4,2.5,5.9,6.8,6.9,8.1,3.8,4.0999999999999996,4,2.6]
[null,13,7.78,9.3699999999999992,10.29,12.48,5.45,5.6,4.95,3.59,9.09,10.199999999999999,7.5,8.41,5.94,6.9,6.4,8.9,4.0999999999999996,6.1,3.9,2.1]
[null,14,7.82,9.27,8.39,27.09,5.25,5.4,5.14,4.08,9.3000000000000007,11.2,6.9,17.149999999999999,6.06,6.1,5.2,9.52,4.0999999999999996,6.7,3.9,2.1]
[null,15,7.75,8.9700000000000006,8.19,8.6999999999999993,5.31,5.4,4.95,3.8,9.2899999999999991,11.2,5.6,17.12,5.92,6.1,5,8.7100000000000009,3.9,5.2,3.9,1.8]
[null,16,7.68,10.69,9.09,4.43,5.24,5.3,6.1,3.95,9.19,9.6,5.4,5.36,5.7,6.3,4.8,6.87,3.7,4.4000000000000004,4.0999999999999996,1.8]
[null,17,6.63,8.9700000000000006,5.59,4.2699999999999996,5.31,5.4,7.24,4.2300000000000004,8.89,8,7.3,3.67,5.23,6.3,4.9000000000000004,5.65,3.8,4.7,4.0999999999999996,3.6]
[null,18,5.5,9.27,0,4.2699999999999996,5.28,5.5,6.86,4.68,7.89,7.6,8.8000000000000007,10.54,4.9400000000000004,6.2,5,5.77,5.6,4.7,5.7,7.2]
[null,19,4.8099999999999996,3.89,0,3.78,5.07,5.6,6.1,5.36,1.8,0,9.1,13.54,4.7,5.8,5,4.97,9.9,12.5,6.1,8.5]
[null,20,3.52,0.4,0,3.94,4.63,5.2,5.33,7.48,0.2,0,0,1.19,4.1500000000000004,3.2,3.5,3.9,9.8000000000000007,13.8,6.1,11.8]
[null,21,2.65,0.4,0,0,4.33,5.2,1.52,8.57,0.1,0,0,0,3.08,3.1,3.5,2.23,9.3000000000000007,12,6.2,13.3]
[null,22,1.88,0,0,0,4.37,4.7,1.1399999999999999,8.9700000000000006,0.1,0,0,0,2.6,3,3.6,1.29,7.9,6.7,6,11.3]
[null,23,0.99,0,0,0,3.14,4.2,0,7.73,0.1,0,0,0,2.42,2.8,4,1.03,6.5,5.9,5.8,9]
[null,24,0.82,0,0,0,2.81,3.6,2.67,4.96,0.1,0,0,0,2.19,1.6,0.2,1.06,1.3,0.3,5.6,6.6]
[null,"日計",{"$f":"SUM(C79:C102)","v":100},100,100.00000000000001,100,100,100,100,100,99.999999999999972,100,99.999999999999986,100,100,99.999999999999986,100,100.00000000000001,100,100.00000000000001,99.999999999999986,100,0,0,0,0]
[null,"最大",{"$f":"IF(MAX(C79:C102)=0,1,MAX(C79:C102))","v":7.82},10.69,16.989999999999998,27.09,5.55,5.6,7.24,8.9700000000000006,9.3000000000000007,11.2,16.899999999999999,17.149999999999999,6.07,6.9,10.3,10.07,9.9,13.8,6.2,13.3,1,1,1,1]
[null,"出典","ku 夏期","ku 夏期","ku 冬期","ku 冬期","ku 夏期","to","ku 冬期","ku","ku 夏期","ku","ku","ku","ku 夏期","ku 夏期","ku 冬期","ku 冬期","ku 夏期","ku","ku","ku 冬期"]

{"sheet":"想定負荷","index":1,"n_rows":158,"n_cols":32,"rows_kept":158,"cut":false,"hidden":false,"merged":[]}
[]
[null,"(４）ピ－ク負荷"]
[]
[null,"時刻",null,null,"夏季",null,null,null,null,"冬期"]
[null,null,"電力","冷房","暖房","給湯","暖房＋給湯","電力","冷房","暖房","給湯","暖房＋給湯"]
[null,null,"kW","kW","kW","kW","kW","kW","kW","kW","kW","kW"]
[null,1,98.951406649616359,0,0,0,0,70.803652173913036,0,0,0,0]
[null,{"$f":"B7+1","v":2},93.52941176470587,0,0,0,0,66.924000000000007,0,0,0,0]
[null,3,93.52941176470587,0,0,0,0,66.924000000000007,0,0,0,0]
[null,4,93.52941176470587,0,0,0,0,66.924000000000007,0,0,0,0]
[null,5,93.52941176470587,0,0,0,0,66.924000000000007,0,0,0,0]
[null,6,119.28388746803068,0,0,0,0,85.352347826086955,0,0,0,0]
[null,7,252.12276214833761,0,0,0.82834190007021513,0.82834190007021513,180.40382608695654,0,24.720423778693352,6.981173864894795,31.701597643588148]
[null,8,760.43478260869563,391.82413470533209,0,0.13875778021480759,0.13875778021480759,544.12121739130441,0,1400,1.169435215946844,1401.1694352159468]
[null,9,992.22506393861897,2094.8362956033679,0,0.68958411985540735,0.68958411985540735,709.97634782608702,0,1012.7133608004709,5.8117386489479506,1018.5250994494189]
[null,10,1035.6010230179027,2007.2778297474276,0,2.7625412606402606,2.7625412606402606,741.01356521739137,0,666.62742789876404,23.282392026578073,689.90981992534216]
[null,11,1038.3120204603581,1963.4985968194576,0,2.4177492007125565,2.4177492007125565,742.95339130434786,0,847.91053560918192,20.376522702104097,868.28705831128605]
[null,12,1045.0895140664961,2029.1674462114124,0,6.2146666411359286,6.2146666411359286,747.80295652173913,0,864.39081812831091,52.37652270210409,916.76734083041504]
[null,13,1054.5780051150896,2051.0570626753974,0,5.2475669608509063,5.2475669608509063,754.59234782608701,0,847.91053560918192,44.225913621262457,892.13644923044433]
[null,14,1060,2029.1674462114124,0,11.390752321270115,11.390752321270115,758.47200000000009,0,691.34785167745747,96,787.34785167745747]
[null,15,1050.5115089514065,1963.4985968194576,0,3.6581596602085633,3.6581596602085633,751.68260869565222,0,674.86756915832848,30.830564784053152,705.69813394238167]
[null,16,1041.0230179028133,2340,0,1.862718079853326,1.862718079853326,744.89321739130435,0,749.02884049440854,15.698781838316721,764.72762233272522]
[null,17,898.695652173913,1963.4985968194576,0,1.7954415803552377,1.7954415803552377,643.05234782608704,0,460.62389640965279,15.131782945736433,475.75567935538925]
[null,18,745.52429667519175,2029.1674462114124,0,1.7954415803552377,1.7954415803552377,533.45217391304345,0,0,15.131782945736433,15.131782945736433]
[null,19,651.99488491048589,851.50608044901787,0,1.5894073006423415,1.5894073006423415,466.52817391304347,0,0,13.395348837209301,13.395348837209301]
[null,20,477.13554987212274,87.558465855940142,0,1.6566838001404303,1.6566838001404303,341.40939130434782,0,0,13.96234772978959,13.96234772978959]
[null,21,359.20716112531966,87.558465855940142,0,0,0,257.02695652173912,0,0,0,0]
[null,22,254.83375959079282,0,0,0,0,182.34365217391306,0,0,0,0]
[null,23,134.19437340153453,0,0,0,0,96.02139130434783,0,0,0,0]
[null,24,111.15089514066496,0,0,0,0,79.532869565217396,0,0,0,0]
[null,"計",{"$f":"SUM(C7:C30)","v":13554.987212276215},21889.616463985036,0,42.047812186305329,42.047812186305329,9699.1304347826081,0,8240.1412595644506,354.37430786267998,8594.5155674271318]
[null,"註）夏季：暖房、給湯は８月の平均日負荷"]
[null,"　　冬期：電力、冷房は１月の平均日負荷"]
[]
[]
[null,"(５）月別負荷（平均日）"]
[]
[null,"時刻",null,null,"１月",null,null,null,null,"２月",null,null,null,null,"３月",null,null,null,null,"４月",null,null,null,null,"５月",null,null,null,null,"６月"]
[null,null,"電力","冷房","暖房","給湯","暖房＋給湯","電力","冷房","暖房","給湯","暖房＋給湯","電力","冷房","暖房","給湯","暖房＋給湯","電力","冷房","暖房","給湯","暖房＋給湯","電力","冷房","暖房","給湯","暖房＋給湯","電力","冷房","暖房","給湯","暖房＋給湯"]
[null,null,"kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW"]
[null,1,70.803652173913036,0,0,0,0,73.576382608695653,0,0,0,0,74.249759999999995,0,0,0,0,74.971000000000004,0,0,0,0,83.13239999999999,0,0,0,0,81.538079999999994,0,0,0,0]
[null,{"$f":"B41+1","v":2},66.924000000000007,0,0,0,0,69.544799999999995,0,0,0,0,70.181280000000001,0,0,0,0,70.863,0,0,0,0,78.577199999999976,0,0,0,0,77.070239999999984,0,0,0,0]
[null,3,66.924000000000007,0,0,0,0,69.544799999999995,0,0,0,0,70.181280000000001,0,0,0,0,70.863,0,0,0,0,78.577199999999976,0,0,0,0,77.070239999999984,0,0,0,0]
[null,4,66.924000000000007,0,0,0,0,69.544799999999995,0,0,0,0,70.181280000000001,0,0,0,0,70.863,0,0,0,0,78.577199999999976,0,0,0,0,77.070239999999984,0,0,0,0]
[null,5,66.924000000000007,0,0,0,0,69.544799999999995,0,0,0,0,70.181280000000001,0,0,0,0,70.863,0,0,0,0,78.577199999999976,0,0,0,0,77.070239999999984,0,0,0,0]
[null,6,85.352347826086955,0,0,0,0,88.694817391304341,0,0,0,0,89.506559999999993,0,0,0,0,90.376000000000005,0,0,0,0,100.2144,0,0,0,0,98.292479999999998,0,0,0,0]
[null,7,180.40382608695654,0,24.741603379335963,2.9819977065767715,27.723601085912737,187.46859130434783,0,21.489186033695557,2.9819977065767715,24.471183740272327,189.18432000000001,0,16.243501486226954,5.4868757801012595,21.730377266328212,191.02200000000002,0,8.1262034573366755,6.8585947251265749,14.984798182463249,211.8168,0,0,3.1175430568757152,3.1175430568757152,207.75456,0,0,2.7434378900506298,2.7434378900506298]
[null,8,544.12121739130441,0,1401.19947138306,0.49952245846209875,1401.6989938415222,565.42946086956522,0,1217.0042357082914,0.49952245846209875,1217.5037581667536,570.60432000000003,0,919.92363416998637,0.91912132357026177,920.84275549355664,576.14700000000016,0,460.21398913383365,1.1489016544628274,461.36289078829645,638.8667999999999,51.917809187778857,0,0.52222802475583052,0.52222802475583052,626.61455999999998,182.63413815709066,0,0.45956066178513089,0.45956066178513089]
[null,9,709.97634782608702,0,1013.5810184401299,2.4824752481146724,1016.0634936882446,737.77961739130433,0,880.34032118039454,2.4824752481146724,882.82279642850926,744.5318400000001,0,665.44211088576412,4.5677544565309978,670.00986534229514,751.76400000000012,0,332.90346830222575,5.7096930706637474,338.61316137288952,833.60159999999996,277.57175079723106,0,2.5953150321198848,2.5953150321198848,817.61471999999992,976.42944254936174,0,2.2838772282654989,2.2838772282654989]
[null,10,741.01356521739137,0,667.19857112942645,9.9450380366545126,677.14360916608098,770.03227826086959,0,579.4917167086569,9.9450380366545126,589.4367547453113,777.07968000000005,0,438.03309007858684,18.298869987444306,456.33196006603112,784.62800000000004,0,219.13661989951234,22.873587484305382,242.01020738381771,870.04319999999984,265.97000572733634,0,10.397085220138809,10.397085220138809,853.35744,935.61734463716255,0,9.1494349937221529,9.1494349937221529]
[null,11,742.95339130434786,0,848.63699591122349,8.7038004125971753,857.34079632382077,772.04806956521736,0,737.0790809557576,8.7038004125971753,745.78288136835477,779.11392000000001,0,557.1521009775845,16.014992759178803,573.16709373676326,786.68200000000002,0,278.72877858664793,20.018740948973505,298.74751953562145,872.32079999999996,260.16913319238904,0,9.0994277040788649,9.0994277040788649,855.59136000000001,915.21129568106323,0,8.0074963795894014,8.0074963795894014]
[null,12,747.80295652173913,0,865.13139816411422,22.372551321423696,887.50394948553787,777.08754782608685,0,751.40520497822126,22.372551321423696,773.77775629964492,784.19952000000001,0,567.98110196840253,41.165494431419596,609.1465963998221,791.81700000000001,0,284.14624755820574,51.456868039274504,335.60311559748027,878.01479999999992,268.87044199481005,0,23.389485472397499,23.389485472397499,861.17615999999987,945.82036911521232,0,20.582747215709798,20.582747215709798]
[null,13,754.59234782608701,0,848.63699591122349,18.891031156384827,867.52802706760838,784.14281739130433,0,737.0790809557576,18.891031156384827,755.97011211214249,791.31936000000007,0,557.1521009775845,34.759497327748079,591.91159830533252,799.00600000000009,0,278.72877858664793,43.449371659685106,322.17815024633308,885.98639999999989,271.7708782622837,0,19.749714390765956,19.749714390765956,868.99487999999997,956.02339359326209,0,17.379748663874039,17.379748663874039]
[null,14,758.47200000000009,0,691.94017450876254,41.006252726479566,732.94642723524203,788.17439999999999,0,600.98090274235244,41.006252726479566,641.98715546883204,795.3878400000001,0,454.27659156481383,75.451505016722393,529.72809658153619,803.11400000000015,0,227.26282335684903,94.314381270903013,321.57720462775205,890.54160000000002,268.87044199481005,0,42.870173304955905,42.870173304955905,873.46271999999999,945.82036911521232,0,37.725752508361197,37.725752508361197]
[null,15,751.68260869565222,0,675.44577225587182,13.16922845036442,688.61500070623617,781.11913043478262,0,586.65477871988867,13.16922845036442,599.82400717025314,788.26800000000003,0,443.4475905739958,24.231380348670534,467.67897092266634,795.92499999999995,0,221.84535438529122,30.289225435838173,252.13457982112939,882.56999999999994,260.16913319238904,0,13.767829743562805,13.767829743562805,865.64399999999989,915.21129568106323,0,12.115690174335267,12.115690174335267]
[null,16,744.89321739130435,0,749.67058239387973,6.7057105787487794,756.37629297262845,774.06386086956513,0,651.12233682097542,6.7057105787487794,657.82804739972414,781.14816000000008,0,492.17809503267665,12.338507464897756,504.51660249757441,788.73599999999999,0,246.22396475730127,15.423134331122196,261.64709908842343,874.59839999999986,310.05663699293621,0,7.0105156050555433,7.0105156050555433,857.82527999999991,1090.7033167035188,0,6.1692537324488779,6.1692537324488779]
[null,17,643.05234782608704,0,461.01854296829345,6.4635178716156414,467.48206083990908,668.23481739130432,0,400.41516642786053,6.4635178716156414,406.87868429947622,674.35056000000009,0,302.67057769336219,11.892872883772778,314.56345057713503,680.90099999999995,0,151.41825775504006,14.866091104715975,166.28434885975605,755.0243999999999,260.16913319238904,0,6.7573141385072617,6.7573141385072617,740.54448000000002,915.21129568106323,0,5.9464364418863891,5.9464364418863891]
[null,18,533.45217391304345,0,0,6.4635178716156414,6.4635178716156414,554.34260869565207,0,0,6.4635178716156414,6.4635178716156414,559.41600000000005,0,0,11.892872883772778,11.892872883772778,564.85,0,0,14.866091104715975,14.866091104715975,626.34,268.87044199481005,0,6.7573141385072617,6.7573141385072617,614.32799999999997,945.82036911521232,0,5.9464364418863891,5.9464364418863891]
[null,19,466.52817391304347,0,0,5.7218027060204033,5.7218027060204033,484.79780869565212,0,0,5.7218027060204033,5.7218027060204033,489.23471999999998,0,0,10.528116979077542,10.528116979077542,493.98700000000002,0,0,13.16014622384693,13.16014622384693,547.76279999999997,112.82697080472612,0,5.9818846472031488,5.9818846472031488,537.25775999999985,396.89765219613554,0,5.2640584895387708,5.2640584895387708]
[null,20,341.40939130434782,0,0,5.9639954131535431,5.9639954131535431,354.77926956521736,0,0,5.9639954131535431,5.9639954131535431,358.02623999999997,0,0,10.973751560202519,10.973751560202519,361.50400000000002,0,0,13.71718945025315,13.71718945025315,400.85759999999999,11.601745069894717,0,6.2350861137514304,6.2350861137514304,393.16991999999999,40.812097912199029,0,5.4868757801012595,5.4868757801012595]
[null,21,257.02695652173912,0,0,0,0,267.09234782608689,0,0,0,0,269.53679999999997,0,0,0,0,272.15499999999997,0,0,0,0,301.78199999999993,11.601745069894717,0,0,0,295.99439999999998,40.812097912199029,0,0,0]
[null,22,182.34365217391306,0,0,0,0,189.48438260869563,0,0,0,0,191.21856,0,0,0,0,193.07599999999999,0,0,0,0,214.09439999999998,0,0,0,0,209.98847999999998,0,0,0,0]
[null,23,96.02139130434783,0,0,0,0,99.781669565217385,0,0,0,0,100.69488,0,0,0,0,101.673,0,0,0,0,112.74119999999999,0,0,0,0,110.57903999999999,0,0,0,0]
[null,24,79.532869565217396,0,0,0,0,82.647443478260854,0,0,0,0,83.403840000000002,0,0,0,0,84.213999999999999,0,0,0,0,93.381599999999992,0,0,0,0,91.59071999999999,0,0,0,0]
[null,"計",{"$f":"SUM(C41:C64)","v":9699.1304347826081},0,8247.2011264453213,151.37044195821176,8398.5715684035349,10078.95652173913,0,7163.062011231852,151.37044195821176,7314.4324531900638,10171.199999999999,0,5414.5004954089845,278.52161320310961,5693.0221086120937,10270.000000000002,0,2708.7344857788917,348.15201650388701,3056.8865022827786,11388,2900.4362674736785,0,158.25091659267591,158.25091659267591,11169.6,10203.024478049756,0,139.2608066015548,139.2608066015548]
[]
[]
[null,"時刻",null,null,"７月",null,null,null,null,"８月",null,null,null,null,"９月",null,null,null,null,"１０月",null,null,null,null,"１１月",null,null,null,null,"１２月"]
[null,null,"電力","冷房","暖房","給湯","暖房＋給湯","電力","冷房","暖房","給湯","暖房＋給湯","電力","冷房","暖房","給湯","暖房＋給湯","電力","冷房","暖房","給湯","暖房＋給湯","電力","冷房","暖房","給湯","暖房＋給湯","電力","冷房","暖房","給湯","暖房＋給湯"]
[null,null,"kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW","kW"]
[null,1,88.213200000000001,0,0,0,0,97.738747826086936,0,0,0,0,88.034191304347829,0,0,0,0,78.896063999999996,0,0,0,0,71.496834782608701,0,0,0,0,72.883200000000002,0,0,0,0]
[null,{"$f":"B71+1","v":2},83.379599999999996,0,0,0,0,92.383199999999988,0,0,0,0,83.210399999999993,0,0,0,0,74.572991999999999,0,0,0,0,67.5792,0,0,0,0,68.889599999999987,0,0,0,0]
[null,3,83.379599999999996,0,0,0,0,92.383199999999988,0,0,0,0,83.210399999999993,0,0,0,0,74.572991999999999,0,0,0,0,67.5792,0,0,0,0,68.889599999999987,0,0,0,0]
[null,4,83.379599999999996,0,0,0,0,92.383199999999988,0,0,0,0,83.210399999999993,0,0,0,0,74.572991999999999,0,0,0,0,67.5792,0,0,0,0,68.889599999999987,0,0,0,0]
[null,5,83.379599999999996,0,0,0,0,92.383199999999988,0,0,0,0,83.210399999999993,0,0,0,0,74.572991999999999,0,0,0,0,67.5792,0,0,0,0,68.889599999999987,0,0,0,0]
[null,6,106.33919999999999,0,0,0,0,117.82205217391304,0,0,0,0,106.12340869565217,0,0,0,0,95.107584000000003,0,0,0,0,86.187965217391309,0,0,0,0,87.859200000000001,0,0,0,0]
[null,7,224.76240000000001,0,0,2.6379210481256052,2.6379210481256052,249.03297391304346,0,0,2.9819977065767715,2.9819977065767715,224.30629565217393,0,0,2.9819977065767715,2.9819977065767715,201.02284800000004,0,0,2.7434378900506298,2.7434378900506298,182.17001739130433,0,7.317939027690918,5.3675958718381889,12.685534899529106,185.70239999999998,0,13.914731947494307,2.2861982417088584,16.200930189203167]
[null,8,677.91240000000005,309.6424597025437,0,0.44188525171647197,0.44188525171647197,751.1155826086956,389.17626620972112,0,0.49952245846209875,0.49952245846209875,676.53673043478273,250.70958034799418,0,0.49952245846209875,0.49952245846209875,606.31084799999996,26.456891743241595,0,0.45956066178513089,0.45956066178513089,549.44827826086953,0,414.43928026822897,0.89914042523177795,415.33842069346071,560.10239999999999,0,788.03765262642742,0.38296721815427581,788.42061984458167]
[null,9,884.54880000000003,1655.4627594152755,0,2.1960357964091335,2.1960357964091335,980.06525217391311,2080.6798143167775,0,2.4824752481146724,2.4824752481146724,882.75380869565231,1340.3858569443041,0,2.4824752481146724,2.4824752481146724,791.12217600000008,141.44829831442573,0,2.2838772282654989,2.2838772282654989,716.92716521739135,0,299.79156883440459,4.4684554466064119,304.260024281011,730.8288,0,570.04018544901669,1.9032310235545824,571.94341647257124]
[null,10,923.21759999999995,1586.2689136716904,0,8.797533647809761,8.797533647809761,1022.9096347826086,1993.7130509179569,0,9.9450380366545126,9.9450380366545126,921.34413913043488,1284.361369715702,0,9.9450380366545126,9.9450380366545126,825.70675199999994,135.53614373493039,0,9.1494349937221529,9.1494349937221529,748.26824347826084,0,197.34042244673176,17.901068465978128,215.24149091270988,762.77760000000001,0,375.23393818409647,7.6245291614351274,382.85846734553161]
[null,11,925.63440000000003,1551.6719907998979,0,7.6995157496051929,7.6995157496051929,1025.5874086956521,1950.2296692185469,0,8.7038004125971753,8.7038004125971753,923.75603478260871,1256.3491261014012,0,8.7038004125971753,8.7038004125971753,827.86828800000001,132.58006644518272,0,8.0074963795894014,8.0074963795894014,750.22706086956521,0,251.00530864979848,15.666840742674918,266.67214939247339,764.77440000000001,0,477.27530579905471,6.6729136496578354,483.94821944871256]
[null,12,931.67640000000006,1603.5673751075867,0,19.791103092028653,19.791103092028653,1032.2818434782607,2015.4547417676622,0,22.372551321423696,22.372551321423696,929.7857739130435,1298.3674915228526,0,22.372551321423696,22.372551321423696,833.27212800000007,137.01418237980423,0,20.582747215709798,20.582747215709798,755.12410434782612,0,255.88393466825912,40.270592378562661,296.15452704682178,769.76639999999998,0,486.55179376405096,17.152289346424837,503.70408311047578]
[null,13,940.13520000000005,1620.8658365434828,0,16.711296792186577,16.711296792186577,1041.654052173913,2037.196432617367,0,18.891031156384827,18.891031156384827,938.22740869565223,1312.3736133300029,0,18.891031156384827,18.891031156384827,840.83750400000008,138.49222102467803,0,17.379748663874039,17.379748663874039,761.97996521739128,0,251.00530864979848,34.003856081492692,285.00916473129121,776.75519999999995,0,477.27530579905471,14.483123886561701,491.75842968561642]
[null,14,944.9688000000001,1603.5673751075867,0,36.274762027270384,36.274762027270384,1047.0095999999999,2015.4547417676622,0,41.006252726479566,41.006252726479566,943.05120000000011,1298.3674915228526,0,41.006252726479566,41.006252726479566,845.16057599999999,137.01418237980423,0,37.725752508361197,37.725752508361197,765.89760000000001,0,204.65836147442269,73.811254907663226,278.46961638208592,780.74880000000007,0,389.14867013159079,31.438127090301002,420.5867972218918]
[null,15,936.51,1551.6719907998979,0,11.649702090706986,11.649702090706986,1037.6373913043478,1950.2296692185469,0,13.16922845036442,13.16922845036442,934.60956521739138,1256.3491261014012,0,13.16922845036442,13.16922845036442,837.59520000000009,132.58006644518272,0,12.115690174335267,12.115690174335267,759.04173913043485,0,199.77973545596208,23.704611210655962,223.48434666661805,773.76,0,379.87218216659454,10.096408478612725,389.96859064520726]
[null,16,928.05119999999999,1849.2055274973138,0,5.931974742739305,5.931974742739305,1028.2651826086956,2324.1867518334743,0,6.7057105787487794,6.7057105787487794,926.16793043478265,1497.2544211843899,0,6.7057105787487794,6.7057105787487794,830.02982400000008,158.00233113701262,0,6.1692537324488779,6.1692537324488779,752.18587826086957,0,221.7335525390348,12.070279041747806,233.8038315807826,766.77119999999991,0,421.61637800907749,5.1410447770407321,426.75742278611824]
[null,17,801.16919999999993,1551.6719907998979,0,5.7177273479676822,5.7177273479676822,887.68205217391301,1950.2296692185469,0,6.4635178716156414,6.4635178716156414,799.54340869565226,1256.3491261014012,0,6.4635178716156414,6.4635178716156414,716.54918399999997,132.58006644518272,0,5.9464364418863891,5.9464364418863891,649.34796521739122,0,136.35759721597412,11.634332168908157,147.99192938488227,661.93919999999991,0,259.27783862164392,4.9553637015719927,264.23320232321589]
[null,18,664.62,1603.5673751075867,0,5.7177273479676822,5.7177273479676822,736.38782608695647,2015.4547417676622,0,6.4635178716156414,6.4635178716156414,663.27130434782612,1298.3674915228526,0,6.4635178716156414,6.4635178716156414,594.42240000000004,137.01418237980423,0,5.9464364418863891,5.9464364418863891,538.67478260869564,0,0,11.634332168908157,11.634332168908157,549.12,0,0,4.9553637015719927,4.9553637015719927]
[null,19,581.24040000000002,672.91014985636593,0,5.0615947014795877,5.0615947014795877,644.00462608695648,845.75177405352815,0,5.7218027060204033,5.7218027060204033,580.06090434782607,544.83813829815506,0,5.7218027060204033,5.7218027060204033,519.84940799999993,57.495703285592064,0,5.2640584895387708,5.2640584895387708,471.09558260869562,0,0,10.299244870836729,10.299244870836729,480.23039999999997,0,0,4.3867154079489765,4.3867154079489765]
[null,20,425.35679999999996,69.193845743585186,0,5.2758420962512105,5.2758420962512105,471.28820869565214,86.966763398820376,0,5.9639954131535431,5.9639954131535431,424.49363478260869,56.024487228602062,0,5.9639954131535431,5.9639954131535431,380.43033600000001,5.9121545794953274,0,5.4868757801012595,5.4868757801012595,344.75186086956523,0,0,10.735191743676378,10.735191743676378,351.43680000000001,0,0,4.5723964834177169,4.5723964834177169]
[null,21,320.226,69.193845743585186,0,0,0,354.80504347826081,86.966763398820376,0,0,0,319.57617391304353,56.024487228602062,0,0,0,286.40352000000001,5.9121545794953274,0,0,0,259.54330434782611,0,0,0,0,264.57600000000002,0,0,0,0]
[null,22,227.17919999999998,0,0,0,0,251.7107478260869,0,0,0,0,226.71819130434784,0,0,0,0,203.18438399999999,0,0,0,0,184.12883478260866,0,0,0,0,187.69919999999999,0,0,0,0]
[null,23,119.63160000000001,0,0,0,0,132.54980869565216,0,0,0,0,119.3888347826087,0,0,0,0,106.996032,0,0,0,0,96.961460869565215,0,0,0,0,98.841599999999985,0,0,0,0]
[null,24,99.088800000000006,0,0,0,0,109.78873043478259,0,0,0,0,98.887721739130427,0,0,0,0,88.622975999999994,0,0,0,0,80.311513043478243,0,0,0,0,81.868799999999993,0,0,0,0]
[null,"計",{"$f":"SUM(C71:C94)","v":12084.000000000004},17298.461435896297,0,133.90462173226422,133.90462173226422,13388.869565217394,21741.690849705097,0,151.37044195821176,151.37044195821176,12059.478260869564,14006.121807150514,0,151.37044195821176,151.37044195821176,10807.679999999998,1478.0386448738318,0,139.2608066015548,139.2608066015548,9794.0869565217363,0,2439.3130092303063,272.46679552478111,2711.7798047550873,9984,0,4638.2439824981029,116.05067216796238,4754.2946546660642]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,"※ピーク日負荷と平均日負荷の関係を既存データ、運転日数等を基に再確認してください。"]