{"text_format":"1","workbook":"xlsx","n_sheets":2,"sheets":["フィルタ効率計算","捕集率換算"],"not_rendered":{"charts":4,"images":3,"macros":1,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"フィルタ効率計算","index":0,"n_rows":53,"n_cols":28,"rows_kept":53,"cut":false,"hidden":false,"merged":[[25,14,25,16],[1,1,1,6],[13,1,13,2],[14,1,14,4],[24,1,24,3],[24,5,24,7]]}
[]
[null,"フィルタ効率計算プログラム"]
[]
[null,"計算手順",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"（参考資料）"]
[null,"１．","フィルタ選定時の性能試験法を入力する。（通常は比色法）"]
[null,"２．","粉じん除去率を計算するフィルタの効率欄に、１を入力する。",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"１．空調システムの粉じん量平衡式"]
[null,"３．","既知のデータを入力する。"]
[null,"1）","既知のフィルタ粉じん除去率は該当する除去率１ヶ所に入力する。他の換算値は自動計算される。"]
[null,null,"(フィルタ粉じん除去率を求める計算においては、１．で指定した性能試験法の値が使用される。)"]
[null,"2）","室内発じん量は直接入力するか、在室人員と単位発じん量を入力し自動計算する。"]
[null,"3）","存在しないフィルタ、ダクト経路の入力欄はブランクとする。"]
[null,"４．","入力が済んだら「計算ボタン」を押す。"]
[]
[null,"入出力画面"]
[null,"フィルタ選定時の性能基準",null,null,null,null,"（1:比色法　2:ＤＯＰ法）"]
[]
[]
[]
[null,null,"外気粉じん濃度",null,"mg/m3",null,null,null,null,null,null,null,null,"室内粉じん濃度",null,"mg/m3",null,null,null,null,null,null,"Ｃ：室内粉じん濃度[mg/m3]",null,null,null," ≦0.15 mg/m3 ※"]
[null,null,null,null,null,null,null,null,null,null,null,null,"室内発じん量",null,null,"mg/h",null,null,null,null,null,null,"Ｇ：室内粉じん発生量[mg/h] ※"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"在室人員",null,"人",null,null,null,null,null,null,"　　Ｇ＝ｎＫ"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"単位発じん量",null,"mg/h人",null,null,null,null,null,null,"　　ｎ：在室人員[人]"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"　　Ｋ：単位発じん量[mg/h人] ",null,null,null," ＝2 mg/h人(非喫煙の一般事務室・店舗)　7 mg/h人(喫煙居室) ※"]
[null,null,"風量",null,"m3/h",null,"風量",null,"m3/h",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"引用：改定 特定建築物における建築確認時審査のためのガイドラインP45"]
[null,"効率(計算:１ 入力:ﾌﾞﾗﾝｸ)",null,null,null,"効率(計算:１ 入力:ﾌﾞﾗﾝｸ)",null,null,null,null,null,null,null,null,null,"風量",null,"m3/h",null,null,null,null,"Ｃｏａ：外気粉じん濃度[mg/m3] ",null,null,null," ＝0.1 mg/m3 ※"]
[null,"粉じん除去率",null,null,"%重量法","粉じん除去率",null,null,"%重量法",null,null,null,null,null,"     効率(計算:１ 入力:ﾌﾞﾗﾝｸ)",null,null,null,null,null,null,null,"Ｖｏａ：外気導入量[m3/h]",null,null,null," ＝25～30 m3/h人 ※"]
[null,null,null,null,"%比色法",null,null,null,"%比色法",null,null,null,null,null,null,"粉じん除去率",null,"%重量法",null,null,null,null,"Ｖｒａ：空調機還気量[m3/h]",null,null,null,"※：数値が与えられている場合は、その値を使用する。"]
[null,null,null,null,"%DOP法",null,null,null,"%DOP法",null,null,null,null,null,null,null,null,"%比色法",null,null,null,null,"Ｖｃａ：室内機循環風量[m3/h]"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"%DOP法",null,null,null,null,"ηｉ：外気処理フィルタ粉じん除去率[-]"]
[null,null,null,null,null,null,"註）除じん除去率が\"***\"は、他の性能試験値への換算時に曲線の範囲外になっていることを示す。",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"ηａ：空調機フィルタ粉じん除去率[-]"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"ηｒ：室内機フィルタ粉じん除去率[-]"]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"フィルタを2段設置する場合は下式による総合除去率を用いる。"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"η：総合粉じん除去率"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"η=1-(1-η1 )(1-η2 )"]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"２．フィルタ選定時の性能基準"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"東京都の場合、フィルタ選定において事務所はＤＯＰ法、店舗と外気処理用は比色法を用いることと指導されている。"]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"３．各性能試験毎の捕集率換算"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"各性能試験毎の捕集率換算は下図による。"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"引用：空気調和衛生工学便覧第14版Ⅱ．P423"]

{"sheet":"捕集率換算","index":1,"n_rows":67,"n_cols":17,"rows_kept":67,"cut":false,"hidden":false,"merged":[]}
[]
[]
[null,"重量法","比色法","y1","y2","y3","y4","y5","y6",null,null,"比色法","DOP法","y1","y2","y3","y4"]
[null,31,7,{"$f":"0.0025*B4^2-0.147*B4+9.1884","v":7.0339},null,null,null,null,null,null,null,23.8,0,{"$f":"0.0015*L4^2+0.6524*L4-16.257","v":0.11977999999999867}]
[null,40,7.5,{"$f":"0.0025*B5^2-0.147*B5+9.1884","v":7.3083999999999998},null,null,null,null,null,null,null,30,4.5,4.6649999999999991]
[null,50,8,{"$f":"0.0025*B6^2-0.147*B6+9.1884","v":8.0884},null,null,null,null,null,null,null,36.5,10,9.5539749999999977]
[null,60,9.5,{"$f":"0.0025*B7^2-0.147*B7+9.1884","v":9.3683999999999994},{"$f":"0.0197*B7^2-2.1615*B7+68.27","v":9.5},null,null,null,null,null,null,40,12.5,12.238999999999997]
[null,62,10,null,{"$f":"0.0197*B8^2-2.1615*B8+68.27","v":9.983799999999988},null,null,null,null,null,null,50,20,20.112999999999996]
[null,70,13.5,null,{"$f":"0.0197*B9^2-2.1615*B9+68.27","v":13.494999999999976},null,null,null,null,null,null,60,28,28.286999999999995]
[null,78.5,20,null,{"$f":"0.0197*B10^2-2.1615*B10+68.27","v":19.988574999999983},{"$f":"0.0797*B10^2-11.779*B10+453.46","v":19.939824999999985},null,null,null,null,null,62,30,29.957799999999995]
[null,86,30,null,null,{"$f":"0.0797*B11^2-11.779*B11+453.46","v":29.927199999999914},null,null,null,null,null,70,37,36.760999999999996]
[null,90,39,null,null,{"$f":"0.0797*B12^2-11.779*B12+453.46","v":38.920000000000016},{"$f":"0.5667*B12^2-99.017*B12+4360.2","v":38.940000000000509},null,null,null,null,73.5,40,39.797775000000001,{"$f":"0.0175*L12^2-1.693*L12+69.658","v":39.761875000000003}]
[null,92.5,50,null,null,null,{"$f":"0.5667*B13^2-99.017*B13+4360.2","v":49.954374999999345},null,null,null,null,80,46.5,null,{"$f":"0.0175*L13^2-1.693*L13+69.658","v":46.218000000000018}]
[null,94,60,null,null,null,{"$f":"0.5667*B14^2-99.017*B14+4360.2","v":59.963200000000143},{"$f":"10*B14-880","v":60},null,null,null,83,50,null,{"$f":"0.0175*L14^2-1.693*L14+69.658","v":49.6965},{"$f":"0.0736*L14^2-10.803*L14+439.67","v":50.051399999999887}]
[null,95,70,null,null,null,null,{"$f":"10*B15-880","v":70},{"$f":"90*B15-8480","v":70},null,null,88.5,60,null,null,{"$f":"0.0736*L15^2-10.803*L15+439.67","v":60.058099999999911}]
[null,95.1,80,null,null,null,null,null,{"$f":"90*B16-8480","v":79},null,null,90,63.5,null,null,{"$f":"0.0736*L16^2-10.803*L16+439.67","v":63.559999999999889},{"$f":"0.9762*L16^2-174.42*L16+7854.1","v":63.520000000000437}]
[null,95.2,88,null,null,null,null,null,{"$f":"90*B17-8480","v":88},null,null,92,70,null,null,null,{"$f":"0.9762*L17^2-174.42*L17+7854.1","v":70.01680000000124}]
[null,null,null,null,null,null,null,null,null,null,null,93.5,80,null,null,null,{"$f":"0.9762*L18^2-174.42*L18+7854.1","v":80.014450000000579}]
[null,null,null,null,null,null,null,null,null,null,null,94,84.5,null,null,null,{"$f":"0.9762*L19^2-174.42*L19+7854.1","v":84.323200000000725}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,"比色法","重量法","y1","y2","y3","y4","y5","y6",null,null,"DOP法","比色法","y1","y2","y3","y4"]
[null,7,31,{"$f":"-4.6077*B52^2+87.829*B52-358.45","v":30.575699999999983},null,null,null,null,null,null,null,0,23.8,{"$f":"-0.0029*L52^2+1.3652*L52+23.665","v":23.664999999999999}]
[null,7.5,40,{"$f":"-4.6077*B53^2+87.829*B53-358.45","v":41.084374999999966},null,null,null,null,null,null,null,4.5,30,29.749675]
[null,8,50,{"$f":"-4.6077*B54^2+87.829*B54-358.45","v":49.289199999999937},null,null,null,null,null,null,null,10,36.5,37.027000000000001]
[null,9.5,60,{"$f":"-4.6077*B55^2+87.829*B55-358.45","v":60.080574999999953},{"$f":"-0.1097*B55^2+4.9724*B55+22.929","v":60.266375000000011},null,null,null,null,null,null,12.5,40,40.276875000000004]
[null,10,62,null,{"$f":"-0.1097*B56^2+4.9724*B56+22.929","v":61.683000000000007},null,null,null,null,null,null,20,50,49.808999999999997]
[null,13.5,70,null,{"$f":"-0.1097*B57^2+4.9724*B57+22.929","v":70.063575000000014},null,null,null,null,null,null,28,60,59.616999999999997]
[null,20,78.5,null,{"$f":"-0.1097*B58^2+4.9724*B58+22.929","v":78.497},{"$f":"-0.0161*B58^2+1.5541*B58+53.851","v":78.492999999999995},null,null,null,null,null,30,62,62.010999999999996]
[null,30,86,null,null,{"$f":"-0.0161*B59^2+1.5541*B59+53.851","v":85.984000000000009},null,null,null,null,null,37,70,70.207300000000004]
[null,39,90,null,null,{"$f":"-0.0161*B60^2+1.5541*B60+53.851","v":89.972800000000007},{"$f":"-0.0037*B60^2+0.5548*B60+73.961","v":89.970500000000001},null,null,null,null,40,73.5,73.632999999999996,{"$f":"-0.0143*L60^2+2.2357*L60+6.9286","v":73.476600000000005}]
[null,50,92.5,null,null,null,{"$f":"-0.0037*B61^2+0.5548*B61+73.961","v":92.450999999999993},null,null,null,null,46.5,80,null,{"$f":"-0.0143*L61^2+2.2357*L61+6.9286","v":79.968474999999998}]
[null,60,94,null,null,null,{"$f":"-0.0037*B62^2+0.5548*B62+73.961","v":93.929000000000002},{"$f":"0.1*B62+88","v":94},null,null,null,50,83,null,{"$f":"-0.0143*L62^2+2.2357*L62+6.9286","v":82.9636},{"$f":"-0.009*L62^2+1.5394*L62+28.516","v":82.98599999999999}]
[null,70,95,null,null,null,null,{"$f":"0.1*B63+88","v":95},{"$f":"0.0111*B63+94.222","v":94.998999999999995},null,null,60,88.5,null,null,{"$f":"-0.009*L63^2+1.5394*L63+28.516","v":88.48}]
[null,80,95.1,null,null,null,null,null,{"$f":"0.0111*B64+94.222","v":95.11},null,null,63.5,90,null,null,{"$f":"-0.009*L64^2+1.5394*L64+28.516","v":89.977650000000011},{"$f":"-0.007*L64^2+1.2219*L64+40.684","v":90.048899999999989}]
[null,88,95.2,null,null,null,null,null,{"$f":"0.0111*B65+94.222","v":95.198799999999991},null,null,70,92,null,null,null,{"$f":"-0.007*L65^2+1.2219*L65+40.684","v":91.917000000000002}]
[null,null,null,null,null,null,null,null,null,null,null,80,93.5,null,null,null,{"$f":"-0.007*L66^2+1.2219*L66+40.684","v":93.635999999999996}]
[null,null,null,null,null,null,null,null,null,null,null,84.5,94,null,null,null,{"$f":"-0.007*L67^2+1.2219*L67+40.684","v":93.952799999999996}]