{"text_format":"1","workbook":"xlsx","n_sheets":3,"sheets":["冷却時FANK","加熱時FANK","ＦＣＵ能力表"],"not_rendered":{"charts":2,"images":3,"macros":1,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"冷却時FANK","index":0,"n_rows":67,"n_cols":17,"rows_kept":67,"cut":false,"hidden":false,"merged":[[55,8,55,9],[59,8,59,9],[59,4,59,5],[41,4,41,5],[2,1,2,3],[63,8,63,9],[40,1,41,1],[51,4,51,5],[63,4,63,5],[6,1,7,1],[63,6,63,7],[47,6,47,7],[43,6,43,7],[43,8,43,9],[59,6,59,7],[43,4,43,5],[47,8,47,9],[41,6,41,7],[41,8,41,9],[51,6,51,7],[55,6,55,7],[47,4,47,5],[55,4,55,5],[51,8,51,9]]}
[]
[]
[null,"天井吊り隠蔽型－標準型"]
[]
[null,"入口空気条件DBｉ=",null,27,"℃　WBi=",19.5,"℃　φi=",49.444568634033203,"%　DPi=",15.523347854614258,"℃　xi=",1.1012131348252296E-2,"kg/kg'　Ii=",55.192687210083008,"kJ/kg'　γi=",1.1558166742324829,"kg'/m3"]
[]
[null,"ユニットサイズ","風量","水量","ｺｲﾙ圧損",null,"入口水温(℃)"]
[null,null,null,null,null,null,7]
[null,null,null,null,null,"SH","TH","SHF","Δtw","ｔｗｏ","DBｏ","Xo","Ｉｏ","Δta","WSF","MTD","FA・N・K"]
[null,null,"m3/h","L/min","kPa","kW","kW","－","℃","℃","℃","kg/kg'","kJ/kg'","℃","－","℃","kW/℃"]
[null,null,335,2,1.3,1.23,1.32,{"$f":"F11/G11","v":0.93181818181818177},{"$f":"G11*860/(D11*60)","v":9.4600000000000009},{"$f":"G$8+I11","v":16.46},15.851754188537598,1.0677292943000793E-2,42.920049121856692,{"$f":"D$5-K11","v":11.148245811462402},{"$f":"1.04*H11^2-2.63*H11+2.59","v":1.0423347107438019},{"$f":"(D$5-J11-K11+G$8)/LN((D$5-J11)/(K11-G$8))","v":9.6713309426512541},{"$f":"G11/(O11*P11)","v":0.13094245711692984}]
[null,200,{"$f":"C11","v":335},4,4.4000000000000004,1.41,1.8,{"$f":"F12/G12","v":0.78333333333333321},{"$f":"G12*860/(D12*60)","v":6.45},{"$f":"G$8+I12","v":13.45},14.246516227722168,9.561171755194664E-3,38.457274175643917,{"$f":"D$5-K12","v":12.753483772277832},{"$f":"1.04*H12^2-2.63*H12+2.59","v":1.1679888888888887},{"$f":"(D$5-J12-K12+G$8)/LN((D$5-J12)/(K12-G$8))","v":10.071623398845043},{"$f":"G12/(O12*P12)","v":0.15301510887273476}]
[null,null,{"$f":"C12","v":335},6,8.8000000000000007,1.5,2.0299999999999998,{"$f":"F13/G13","v":0.73891625615763556},{"$f":"G13*860/(D13*60)","v":4.849444444444444},{"$f":"G$8+I13","v":11.849444444444444},13.440571784973145,9.0403156355023384E-3,36.318860265731814,{"$f":"D$5-K13","v":13.559428215026855},{"$f":"1.04*H13^2-2.63*H13+2.59","v":1.2144873692639957},{"$f":"(D$5-J13-K13+G$8)/LN((D$5-J13)/(K13-G$8))","v":10.182115221848926},{"$f":"G13/(O13*P13)","v":0.16415912485701584}]
[null,null,{"$f":"C13","v":335},8,14.4,1.55,2.16,{"$f":"F14/G14","v":0.71759259259259256},{"$f":"G14*860/(D14*60)","v":3.87},{"$f":"G$8+I14","v":10.870000000000001},12.992364883422852,8.7426817044615746E-3,35.11018997192383,{"$f":"D$5-K14","v":14.007635116577148},{"$f":"1.04*H14^2-2.63*H14+2.59","v":1.2382681755829905},{"$f":"(D$5-J14-K14+G$8)/LN((D$5-J14)/(K14-G$8))","v":10.23802144896235},{"$f":"G14/(O14*P14)","v":0.17038172258009546}]
[null,null,480,3,3.1,1.77,1.91,{"$f":"F15/G15","v":0.92670157068062831},{"$f":"G15*860/(D15*60)","v":9.1255555555555556},{"$f":"G$8+I15","v":16.125555555555557},15.804347991943359,1.0648615658283234E-2,42.798989274978638,{"$f":"D$5-K15","v":11.195652008056641},{"$f":"1.04*H15^2-2.63*H15+2.59","v":1.0459017022559687},{"$f":"(D$5-J15-K15+G$8)/LN((D$5-J15)/(K15-G$8))","v":9.8029947756157636},{"$f":"G15/(O15*P15)","v":0.18628750504754993}]
[null,300,{"$f":"C15","v":480},6,10.3,1.99,2.5,{"$f":"F16/G16","v":0.79600000000000004},{"$f":"G16*860/(D16*60)","v":5.9722222222222223},{"$f":"G$8+I16","v":12.972222222222221},14.435543060302734,9.6878986805677414E-3,38.970571918487551,{"$f":"D$5-K16","v":12.564456939697266},{"$f":"1.04*H16^2-2.63*H16+2.59","v":1.1554806399999999},{"$f":"(D$5-J16-K16+G$8)/LN((D$5-J16)/(K16-G$8))","v":10.385268383844798},{"$f":"G16/(O16*P16)","v":0.20833374030050417}]
[null,null,{"$f":"C16","v":480},9,20.9,2.09,2.77,{"$f":"F17/G17","v":0.75451263537906132},{"$f":"G17*860/(D17*60)","v":4.4114814814814816},{"$f":"G$8+I17","v":11.411481481481481},13.811909675598145,9.2464881017804146E-3,37.218583435058591,{"$f":"D$5-K17","v":13.188090324401855},{"$f":"1.04*H17^2-2.63*H17+2.59","v":1.1976926585775911},{"$f":"(D$5-J17-K17+G$8)/LN((D$5-J17)/(K17-G$8))","v":10.601534164359647},{"$f":"G17/(O17*P17)","v":0.21815524768920067}]
[null,null,{"$f":"C17","v":480},12,34.299999999999997,2.15,2.92,{"$f":"F18/G18","v":0.73630136986301364},{"$f":"G18*860/(D18*60)","v":3.4877777777777776},{"$f":"G$8+I18","v":10.487777777777778},13.436496734619141,9.0127997100353241E-3,36.245254281997681,{"$f":"D$5-K18","v":13.563503265380859},{"$f":"1.04*H18^2-2.63*H18+2.59","v":1.2173526928129106},{"$f":"(D$5-J18-K18+G$8)/LN((D$5-J18)/(K18-G$8))","v":10.694777262103839},{"$f":"G18/(O18*P18)","v":0.22428213760537399}]
[null,null,725,4,2.2000000000000002,2.62,2.72,{"$f":"F19/G19","v":0.96323529411764708},{"$f":"G19*860/(D19*60)","v":9.7466666666666679},{"$f":"G$8+I19","v":16.74666666666667},16.02296257019043,1.0840221308171749E-2,43.507391977310178,{"$f":"D$5-K19","v":10.97703742980957},{"$f":"1.04*H19^2-2.63*H19+2.59","v":1.0216262975778547},{"$f":"(D$5-J19-K19+G$8)/LN((D$5-J19)/(K19-G$8))","v":9.6250449818296566},{"$f":"G19/(O19*P19)","v":0.27661394638378012}]
[null,400,{"$f":"C19","v":725},8,7.3,2.95,3.62,{"$f":"F20/G20","v":0.81491712707182318},{"$f":"G20*860/(D20*60)","v":6.4858333333333338},{"$f":"G$8+I20","v":13.485833333333334},14.665139198303223,9.8603451624512672E-3,39.640938076019289,{"$f":"D$5-K20","v":12.334860801696777},{"$f":"1.04*H20^2-2.63*H20+2.59","v":1.1374214767558986},{"$f":"(D$5-J20-K20+G$8)/LN((D$5-J20)/(K20-G$8))","v":10.314729165402953},{"$f":"G20/(O20*P20)","v":0.30855267582540669}]
[null,null,{"$f":"C20","v":725},13,17,3.15,4.13,{"$f":"F21/G21","v":0.76271186440677963},{"$f":"G21*860/(D21*60)","v":4.5535897435897432},{"$f":"G$8+I21","v":11.553589743589743},13.838360786437988,9.3274284154176712E-3,37.449944471359252,{"$f":"D$5-K21","v":13.161639213562012},{"$f":"1.04*H21^2-2.63*H21+2.59","v":1.1890663602413101},{"$f":"(D$5-J21-K21+G$8)/LN((D$5-J21)/(K21-G$8))","v":10.564245898150361},{"$f":"G21/(O21*P21)","v":0.32878005022329082}]
[null,null,{"$f":"C21","v":725},18,29.8,3.25,4.4000000000000004,{"$f":"F22/G22","v":0.73863636363636354},{"$f":"G22*860/(D22*60)","v":3.503703703703704},{"$f":"G$8+I22","v":10.503703703703703},13.425000190734863,9.0351831167936325E-3,36.290005506515506,{"$f":"D$5-K22","v":13.574999809265137},{"$f":"1.04*H22^2-2.63*H22+2.59","v":1.2147933884297522},{"$f":"(D$5-J22-K22+G$8)/LN((D$5-J22)/(K22-G$8))","v":10.680747817832156},{"$f":"G22/(O22*P22)","v":0.33911624587007494}]
[null,null,860,6,5.6,3.34,3.87,{"$f":"F23/G23","v":0.86304909560723508},{"$f":"G23*860/(D23*60)","v":9.245000000000001},{"$f":"G$8+I23","v":16.245000000000001},15.218732833862305,1.0244039818644524E-2,41.176779342651365,{"$f":"D$5-K23","v":11.781267166137695},{"$f":"1.04*H23^2-2.63*H23+2.59","v":1.094828769638577},{"$f":"(D$5-J23-K23+G$8)/LN((D$5-J23)/(K23-G$8))","v":9.4300897462718716},{"$f":"G23/(O23*P23)","v":0.3748425968198339}]
[null,600,{"$f":"C23","v":860},10,13.5,3.64,4.68,{"$f":"F24/G24","v":0.7777777777777779},{"$f":"G24*860/(D24*60)","v":6.7079999999999993},{"$f":"G$8+I24","v":13.707999999999998},14.176037788391113,9.5049347728490829E-3,38.243218809127804,{"$f":"D$5-K24","v":12.823962211608887},{"$f":"1.04*H24^2-2.63*H24+2.59","v":1.1735802469135799},{"$f":"(D$5-J24-K24+G$8)/LN((D$5-J24)/(K24-G$8))","v":9.9218263838124194},{"$f":"G24/(O24*P24)","v":0.40192168522864924}]
[null,null,{"$f":"C24","v":860},15,27.2,3.84,5.18,{"$f":"F25/G25","v":0.74131274131274127},{"$f":"G25*860/(D25*60)","v":4.9497777777777783},{"$f":"G$8+I25","v":11.949777777777779},13.477954864501953,9.0701645240187645E-3,36.432375080108642,{"$f":"D$5-K25","v":13.522045135498047},{"$f":"1.04*H25^2-2.63*H25+2.59","v":1.2118738539974061},{"$f":"(D$5-J25-K25+G$8)/LN((D$5-J25)/(K25-G$8))","v":10.168909094083954},{"$f":"G25/(O25*P25)","v":0.42033734725479227}]
[null,null,{"$f":"C25","v":860},20,44.7,3.95,5.46,{"$f":"F26/G26","v":0.72344322344322343},{"$f":"G26*860/(D26*60)","v":3.9130000000000003},{"$f":"G$8+I26","v":10.913},13.093713760375977,8.8237971067428589E-3,35.418306743621827,{"$f":"D$5-K26","v":13.906286239624023},{"$f":"1.04*H26^2-2.63*H26+2.59","v":1.2316492237920809},{"$f":"(D$5-J26-K26+G$8)/LN((D$5-J26)/(K26-G$8))","v":10.294357238321615},{"$f":"G26/(O26*P26)","v":0.43063207056404357}]
[null,null,1360,8,5.4,5.03,5.44,{"$f":"F27/G27","v":0.92463235294117641},{"$f":"G27*860/(D27*60)","v":9.7466666666666679},{"$f":"G$8+I27","v":16.74666666666667},15.77115535736084,1.0636396706104279E-2,42.734101995468137,{"$f":"D$5-K27","v":11.22884464263916},{"$f":"1.04*H27^2-2.63*H27+2.59","v":1.0473596993944636},{"$f":"(D$5-J27-K27+G$8)/LN((D$5-J27)/(K27-G$8))","v":9.4929672722150045},{"$f":"G27/(O27*P27)","v":0.5471432642660925}]
[null,800,{"$f":"C27","v":1360},14,14.1,5.52,6.75,{"$f":"F28/G28","v":0.81777777777777771},{"$f":"G28*860/(D28*60)","v":6.9107142857142856},{"$f":"G$8+I28","v":13.910714285714285},14.69537353515625,9.8849302157759666E-3,39.733965532302854,{"$f":"D$5-K28","v":12.30462646484375},{"$f":"1.04*H28^2-2.63*H28+2.59","v":1.1347553580246916},{"$f":"(D$5-J28-K28+G$8)/LN((D$5-J28)/(K28-G$8))","v":10.154685744944462},{"$f":"G28/(O28*P28)","v":0.5857806786748232}]
[null,null,{"$f":"C28","v":1360},20,26.2,5.78,7.45,{"$f":"F29/G29","v":0.77583892617449668},{"$f":"G29*860/(D29*60)","v":5.3391666666666664},{"$f":"G$8+I29","v":12.339166666666667},14.123480796813965,9.4817029312252998E-3,38.130837745666504,{"$f":"D$5-K29","v":12.876519203186035},{"$f":"1.04*H29^2-2.63*H29+2.59","v":1.1755467051033739},{"$f":"(D$5-J29-K29+G$8)/LN((D$5-J29)/(K29-G$8))","v":10.442684216560808},{"$f":"G29/(O29*P29)","v":0.60688197529675991}]
[null,null,{"$f":"C29","v":1360},26,41.2,5.94,7.86,{"$f":"F30/G30","v":0.75572519083969469},{"$f":"G30*860/(D30*60)","v":4.3330769230769235},{"$f":"G$8+I30","v":11.333076923076923},13.770661354064941,9.2525975778698921E-3,37.191864439010622,{"$f":"D$5-K30","v":13.229338645935059},{"$f":"1.04*H30^2-2.63*H30+2.59","v":1.1964081347240834},{"$f":"(D$5-J30-K30+G$8)/LN((D$5-J30)/(K30-G$8))","v":10.604006057317264},{"$f":"G30/(O30*P30)","v":0.61954552105343119}]
[null,null,1690,12,12.1,6.51,7.45,{"$f":"F31/G31","v":0.87382550335570464},{"$f":"G31*860/(D31*60)","v":8.8986111111111104},{"$f":"G$8+I31","v":15.89861111111111},15.312984466552734,1.0318901389837265E-2,41.462440660476688,{"$f":"D$5-K31","v":11.687015533447266},{"$f":"1.04*H31^2-2.63*H31+2.59","v":1.0859527769019415},{"$f":"(D$5-J31-K31+G$8)/LN((D$5-J31)/(K31-G$8))","v":9.6400676926047275},{"$f":"G31/(O31*P31)","v":0.71164802599533028}]
[null,1200,{"$f":"C31","v":1690},18,24.4,6.93,8.58,{"$f":"F32/G32","v":0.8076923076923076},{"$f":"G32*860/(D32*60)","v":6.8322222222222226},{"$f":"G$8+I32","v":13.832222222222223},14.570538520812988,9.7952932119369507E-3,39.379867975234987,{"$f":"D$5-K32","v":12.429461479187012},{"$f":"1.04*H32^2-2.63*H32+2.59","v":1.1442307692307696},{"$f":"(D$5-J32-K32+G$8)/LN((D$5-J32)/(K32-G$8))","v":10.112290251082378},{"$f":"G32/(O32*P32)","v":0.7415221684479808}]
[null,null,{"$f":"C32","v":1690},24,40.200000000000003,7.18,9.25,{"$f":"F33/G33","v":0.77621621621621617},{"$f":"G33*860/(D33*60)","v":5.5243055555555554},{"$f":"G$8+I33","v":12.524305555555555},14.127890586853027,9.4855548813939095E-3,38.145069513320919,{"$f":"D$5-K33","v":12.872109413146973},{"$f":"1.04*H33^2-2.63*H33+2.59","v":1.1751634302410516},{"$f":"(D$5-J33-K33+G$8)/LN((D$5-J33)/(K33-G$8))","v":10.371579053955104},{"$f":"G33/(O33*P33)","v":0.75892451635768787}]
[null,null,{"$f":"C33","v":1690},30,59.1,7.35,9.69,{"$f":"F34/G34","v":0.75851393188854488},{"$f":"G34*860/(D34*60)","v":4.6296666666666662},{"$f":"G$8+I34","v":11.629666666666665},13.826322555541992,9.2864343896508217E-3,37.33415417098999,{"$f":"D$5-K34","v":13.173677444458008},{"$f":"1.04*H34^2-2.63*H34+2.59","v":1.1934654793969079},{"$f":"(D$5-J34-K34+G$8)/LN((D$5-J34)/(K34-G$8))","v":10.526677398892479},{"$f":"G34/(O34*P34)","v":0.77129870400121892}]
[]
[null,"☆ FA･N･Kの計算式（冷却時）"]
[]
[null,"入口水温",null,{"$f":"G8","v":7},"℃"]
[null,"入口空気条件",null,{"$f":"D5","v":27},"℃DB",{"$f":"F5","v":19.5},"℃WB"]
[]
[null,"ユニットサイズ","水量","FA・N・K",null,null,"FA・N・K=aL2+bL+c",null,null,null,"FA・N・K","誤差"]
[null,null,"L",null,"a",null,"b",null,"c",null,"計算値"]
[null,null,"L/min","kW/℃",null,null,null,null,null,null,"kW/℃","％"]
[null,null,{"$f":"D11","v":2},{"$f":"Q11","v":0.13094245711692984},-1.1783538537945663E-3,null,1.8106449000669843E-2,null,9.9442974530768419E-2,null,0.13094246387481689,{"$f":"(D44-K44)/D44*100","v":-5.1609594048428485E-6}]
[null,200,{"$f":"D12","v":4},{"$f":"Q12","v":0.15301510887273476},null,null,null,null,null,null,0.15301510691642761,{"$f":"(D45-K45)/D45*100","v":1.2785058668191279E-6}]
[null,null,{"$f":"D13","v":6},{"$f":"Q13","v":0.16415912485701584},null,null,null,null,null,null,0.16566093266010284,{"$f":"(D46-K46)/D46*100","v":-0.91484881172161236}]
[null,null,{"$f":"D14","v":8},{"$f":"Q14","v":0.17038172258009546},null,null,null,null,null,null,0.1688799262046814,{"$f":"(D47-K47)/D47*100","v":0.88143044492819644}]
[null,null,{"$f":"D15","v":3},{"$f":"Q15","v":0.18628750504754993},-5.6067788988401119E-4,null,1.2394846093274205E-2,null,0.15414906777668341,null,0.18628750741481781,{"$f":"(D48-K48)/D48*100","v":-1.2707604200913421E-6}]
[null,300,{"$f":"D16","v":6},{"$f":"Q16","v":0.20833374030050417},null,null,null,null,null,null,0.20833374559879303,{"$f":"(D49-K49)/D49*100","v":-2.543173686391705E-6}]
[null,null,{"$f":"D17","v":9},{"$f":"Q17","v":0.21815524768920067},null,null,null,null,null,null,0.22028777003288269,{"$f":"(D50-K50)/D50*100","v":-0.97752511858901825}]
[null,null,{"$f":"D18","v":12},{"$f":"Q18","v":0.22428213760537399},null,null,null,null,null,null,0.22214961051940918,{"$f":"(D51-K51)/D51*100","v":0.95082341765308587}]
[null,null,{"$f":"D19","v":4},{"$f":"Q19","v":0.27661394638378012},-3.728610341915033E-4,null,1.2459014770704682E-2,null,0.23274366384802544,null,0.27661395072937012,{"$f":"(D52-K52)/D52*100","v":-1.5709945415861736E-6}]
[null,400,{"$f":"D20","v":8},{"$f":"Q20","v":0.30855267582540669},null,null,null,null,null,null,0.30855268239974976,{"$f":"(D53-K53)/D53*100","v":-2.1307036318371848E-6}]
[null,null,{"$f":"D21","v":13},{"$f":"Q21","v":0.32878005022329082},null,null,null,null,null,null,0.33169734477996826,{"$f":"(D54-K54)/D54*100","v":-0.88730887251101809}]
[null,null,{"$f":"D22","v":18},{"$f":"Q22","v":0.33911624587007494},null,null,null,null,null,null,0.33619895577430725,{"$f":"(D55-K55)/D55*100","v":0.86026255931288675}]
[null,null,{"$f":"D23","v":6},{"$f":"Q23","v":0.3748425968198339},-2.9416497366208317E-4,null,1.1476411680797152E-2,null,0.31657406578688602,null,0.37484258413314819,{"$f":"(D56-K56)/D56*100","v":3.3845368188175688E-6}]
[null,600,{"$f":"D24","v":10},{"$f":"Q24","v":0.40192168522864924},null,null,null,null,null,null,0.40192168951034546,{"$f":"(D57-K57)/D57*100","v":-1.0653060974709759E-6}]
[null,null,{"$f":"D25","v":15},{"$f":"Q25","v":0.42033734725479227},null,null,null,null,null,null,0.42253312468528748,{"$f":"(D58-K58)/D58*100","v":-0.5223845667856416}]
[null,null,{"$f":"D26","v":20},{"$f":"Q26","v":0.43063207056404357},null,null,null,null,null,null,0.42843630909919739,{"$f":"(D59-K59)/D59*100","v":0.50989269377224111}]
[null,null,{"$f":"D27","v":8},{"$f":"Q27","v":0.5471432642660925},-2.1196564558027516E-4,null,1.1102813270887833E-2,null,0.47188655941612745,null,0.54714328050613403,{"$f":"(D60-K60)/D60*100","v":-2.9681515965586462E-6}]
[null,800,{"$f":"D28","v":14},{"$f":"Q28","v":0.5857806786748232},null,null,null,null,null,null,0.58578068017959595,{"$f":"(D61-K61)/D61*100","v":-2.5688330216916219E-7}]
[null,null,{"$f":"D29","v":20},{"$f":"Q29","v":0.60688197529675991},null,null,null,null,null,null,0.60915654897689819,{"$f":"(D62-K62)/D62*100","v":-0.37479671051789509}]
[null,null,{"$f":"D30","v":26},{"$f":"Q30","v":0.61954552105343119},null,null,null,null,null,null,0.61727094650268555,{"$f":"(D63-K63)/D63*100","v":0.36713598491973926}]
[null,null,{"$f":"D31","v":12},{"$f":"Q31","v":0.71164802599533028},-1.4737340751631774E-4,null,9.4002259675979253E-3,null,0.62006708506650499,null,0.71164804697036743,{"$f":"(D64-K64)/D64*100","v":-2.9473892128426142E-6}]
[null,1200,{"$f":"D32","v":18},{"$f":"Q32","v":0.7415221684479808},null,null,null,null,null,null,0.74152219295501709,{"$f":"(D65-K65)/D65*100","v":-3.3049634025769558E-6}]
[null,null,{"$f":"D33","v":24},{"$f":"Q33","v":0.75892451635768787},null,null,null,null,null,null,0.76078540086746216,{"$f":"(D66-K66)/D66*100","v":-0.24520021025348379}]
[null,null,{"$f":"D34","v":30},{"$f":"Q34","v":0.77129870400121892},null,null,null,null,null,null,0.76943778991699219,{"$f":"(D67-K67)/D67*100","v":0.24127022054788611}]

{"sheet":"加熱時FANK","index":1,"n_rows":67,"n_cols":17,"rows_kept":67,"cut":false,"hidden":false,"merged":[[63,8,63,9],[40,1,41,1],[63,4,63,5],[43,8,43,9],[41,4,41,5],[41,6,41,7],[41,8,41,9],[51,6,51,7],[2,1,2,3],[6,1,7,1],[59,6,59,7],[63,6,63,7],[47,6,47,7],[51,4,51,5],[43,6,43,7],[55,6,55,7],[47,4,47,5],[43,4,43,5],[55,4,55,5],[59,4,59,5],[47,8,47,9],[51,8,51,9],[55,8,55,9],[59,8,59,9]]}
[]
[]
[null,"天井吊り隠蔽型－標準型"]
[]
[null,"入口空気条件DBｉ=",null,22,"℃　WBi=",15.6,"℃　φi=",50.772289276123047,"%　DPi=",11.340983390808105,"℃　xi=",8.3484482020139694E-3,"kg/kg'　Ii=",43.303484479904171,"kJ/kg'　γi=",1.1803632974624634,"kg'/m3"]
[]
[null,"ユニットサイズ","風量","水量","水圧損失",null,"入口水温(℃)"]
[null,null,null,null,null,null,50]
[null,null,null,null,null,"SH","TH","SHF","Δtw","ｔｗｏ","DBｏ","Xo","Ｉｏ","Δta","WSF","MTD","FA・N・K"]
[null,null,"m3/h","L/min","kPa","kW","kW","－","℃","℃","℃","kg/kg'","kJ/kg'","℃","－","℃","kW/℃"]
[null,null,335,2,1.3,{"$f":"G11","v":1.82},1.82,{"$f":"F11/G11","v":1},{"$f":"G11*860/($D11*60)","v":13.043333333333333},{"$f":"G$8-I11","v":36.956666666666663},{"$f":"$D$5+G11*860/($C11*$P$5*(0.24+0.44*$L$5))","v":38.244313399411517},{"$f":"$L$5","v":8.3484482020139694E-3},{"$f":"(0.24*K11+L11*(597+0.44*L11))*4.186","v":59.285018075204682},{"$f":"K11-P$5","v":37.063950101949054},1,{"$f":"($G$8-K11-J11+$D$5)/LN((G$8-K11)/(J11-$D$5))","v":13.292000292864353},{"$f":"G11/(O11*P11)","v":0.13692446282724238}]
[null,200,{"$f":"C11","v":335},4,4.4000000000000004,2.15,2.15,1,7.7041666666666666,42.295833333333334,41.189710883920199,8.3484482020139694E-3,62.244082204041476,40.009347586457736,1,13.763460945352469,0.15621070954002991]
[null,null,{"$f":"C12","v":335},6,8.8000000000000007,2.27,2.27,1,5.4227777777777781,44.577222222222218,42.260764514650631,8.3484482020139694E-3,63.320105523618501,41.080401217188168,1,13.859005653777814,0.16379241460091495]
[null,null,{"$f":"C13","v":335},8,14.4,2.33,2.33,1,4.1745833333333335,45.825416666666669,42.796291330015841,8.3484482020139694E-3,63.858117183407003,41.615928032553377,1,13.895925593221877,0.16767504865861704]
[null,null,480,3,3.1,2.67,2.67,1,12.756666666666666,37.243333333333332,38.63201250011862,8.3484482020139694E-3,59.674516099739073,37.451649202656156,1,13.21106286203959,0.20210334534641614]
[null,300,{"$f":"C15","v":480},6,10.3,3.09,3.09,1,7.3816666666666668,42.618333333333332,41.248284129350765,8.3484482020139694E-3,62.302927229330848,40.067920831888301,1,13.847811906036281,0.22313994593276246]
[null,null,{"$f":"C16","v":480},9,20.9,3.24,3.24,1,5.16,44.84,42.18266685407653,8.3484482020139694E-3,63.241645489899341,41.002303556614066,1,14.011460867610944,0.23123927123756394]
[null,null,{"$f":"C17","v":480},12,34.299999999999997,3.32,3.32,1,3.9655555555555555,46.034444444444446,42.681004307263606,8.3484482020139694E-3,63.742295228869203,41.500641009801143,1,14.058233579912013,0.23616053760438221]
[null,null,725,4,2.2000000000000002,3.87,3.87,1,13.867500000000001,36.1325,37.960545742074316,8.3484482020139694E-3,58.999933735937439,36.780182444611853,1,13.058031583830324,0.29636932451535775]
[null,400,{"$f":"C19","v":725},8,7.3,4.5599999999999996,4.5599999999999996,1,8.1699999999999982,41.83,40.80622444027361,8.3484482020139694E-3,61.858816383296372,39.625861142811146,1,13.837192450129692,0.32954661983885758]
[null,null,{"$f":"C20","v":725},13,17,4.8600000000000003,4.8600000000000003,1,5.3584615384615386,44.64153846153846,42.043476048186349,8.3484482020139694E-3,63.101808838669818,40.863112750723886,1,14.041976393496054,0.34610512536191484]
[null,null,{"$f":"C21","v":725},18,29.8,5,5,1,3.9814814814814814,46.018518518518519,42.620860131878956,8.3484482020139694E-3,63.681871984510771,41.440496834416493,1,14.099160352937453,0.35463104715723642]
[null,null,860,6,5.6,5.13,5.13,1,12.255000000000001,37.744999999999997,39.835845126858331,8.3484482020139694E-3,60.883934509866847,38.655481829395868,1,12.751683610602109,0.40229981833416673]
[null,600,{"$f":"C23","v":860},10,13.5,5.67,5.67,1,8.1269999999999989,41.873000000000005,41.713302508632893,8.3484482020139694E-3,62.770103293892838,40.532939211170429,1,13.24587093085926,0.42805792307627349]
[null,null,{"$f":"C24","v":860},15,27.2,5.95,5.95,1,5.6855555555555553,44.314444444444447,42.686798928812294,8.3484482020139694E-3,63.748116737461871,41.506435631349831,1,13.447359066991714,0.44246606120640047]
[null,null,{"$f":"C25","v":860},20,44.7,6.09,6.09,1,4.3644999999999996,45.6355,43.173547138901995,8.3484482020139694E-3,64.237123459246391,41.993183841439532,1,13.534457793111084,0.44996261343396809]
[null,null,1360,8,5.4,7.54,7.54,1,13.509166666666665,36.490833333333335,38.577048810428877,8.3484482020139694E-3,59.619297378529161,37.396685512966414,1,12.896130914501896,0.58467148402790758]
[null,800,{"$f":"C27","v":1360},14,14.1,8.5399999999999991,8.5399999999999991,1,8.7433333333333323,41.256666666666668,40.775596398018905,8.3484482020139694E-3,61.828046226925601,39.595233100556442,1,13.63070361750753,0.62652671788938785]
[null,null,{"$f":"C28","v":1360},20,26.2,8.9700000000000006,8.9700000000000006,1,6.4285000000000005,43.5715,41.720971860682624,8.3484482020139694E-3,62.777808231736081,40.540608563220161,1,13.880340190301903,0.64623776341355654]
[null,null,{"$f":"C29","v":1360},26,41.2,9.2100000000000009,9.2100000000000009,1,5.0773076923076923,44.922692307692309,42.248623281704234,8.3484482020139694E-3,63.307907955351233,41.06825998424177,1,13.992362737256718,0.65821621215386483]
[null,null,1690,12,12.1,9.76,9.76,1,11.657777777777778,38.342222222222219,39.26783506428113,8.3484482020139694E-3,60.313288880599288,38.087471766818666,1,13.341181591359749,0.73156938410319983]
[null,1200,{"$f":"C31","v":1690},18,24.4,10.55,10.55,1,8.4009259259259252,41.599074074074075,40.66553892706618,8.3484482020139694E-3,61.717478089307662,39.485175629603717,1,13.838013072627117,0.76239268922710346]
[null,null,{"$f":"C32","v":1690},24,40.200000000000003,10.96,10.96,1,6.5455555555555556,43.454444444444448,41.390929539397661,8.3484482020139694E-3,62.446234514080366,40.210566241935197,1,14.067633698551839,0.77909335961230308]
[null,null,{"$f":"C33","v":1690},30,59.1,11.21,11.21,1,5.3558888888888889,44.644111111111108,41.833240888380274,8.3484482020139694E-3,62.890598187722247,40.652877590917811,1,14.195880698869823,0.7896656951260842]
[]
[null,"☆ FA･N･Kの計算式（加熱時）"]
[]
[null,"入口水温",null,{"$f":"G8","v":50},"℃"]
[null,"入口空気条件",null,{"$f":"D5","v":22},"℃DB",{"$f":"F5","v":15.6},"℃WB"]
[]
[null,"ユニットサイズ","水量","FA・N・K",null,null,"FA・N・K=aL2+bL+c",null,null,null,"FA・N・K","誤差"]
[null,null,"L",null,"a",null,"b",null,"c",null,null,"％"]
[null,null,"L/min","kW/℃"]
[null,null,{"$f":"D11","v":2},{"$f":"Q11","v":0.13692446282724238},-1.2128967657699385E-3,null,1.6920503951013396E-2,null,0.10793504198829534,null,0.13692446053028107,{"$f":"(D44-K44)/D44*100","v":1.677539037340246E-6}]
[null,200,4,0.15621070954002991,null,null,null,null,null,null,0.15621070563793182,2.4979709141469206E-6]
[null,null,6,0.16379241460091495,null,null,null,null,null,null,0.165793776512146,-1.2218892529958847]
[null,null,8,0.16767504865861704,null,null,null,null,null,null,0.16567367315292358,1.1936036528417646]
[null,null,3,0.20210334534641614,-5.8319292704092868E-4,null,1.2260936538817139E-2,null,0.17056927207333308,null,0.20210334658622742,-6.1345411145572227E-7]
[null,300,6,0.22313994593276246,null,null,null,null,null,null,0.22313994169235229,1.9003366448654055E-6]
[null,null,9,0.23123927123756394,null,null,null,null,null,null,0.23367907106876373,-1.0550975265327076]
[null,null,12,0.23616053760438221,null,null,null,null,null,null,0.23372073471546173,1.0331120151020567]
[null,null,4,0.29636932451535775,-4.474158662644348E-4,null,1.3663314226048176E-2,null,0.248874721471396,null,0.29636931419372559,3.4826924739800457E-6]
[null,400,8,0.32954661983885758,null,null,null,null,null,null,0.32954663038253784,-3.1994502833514397E-6]
[null,null,13,0.34610512536191484,null,null,null,null,null,null,0.35088452696800232,-1.3809103812287538]
[null,null,18,0.35463104715723642,null,null,null,null,null,null,0.34985163807868958,1.347713099814341]
[null,null,6,0.40229981833416673,-3.2583817168783892E-4,null,1.1652936932532127E-2,null,0.34411237091973618,null,0.40229982137680054,-7.5631001380172258E-7]
[null,600,10,0.42805792307627349,null,null,null,null,null,null,0.42805790901184082,3.2856377410254101E-6]
[null,null,15,0.44246606120640047,null,null,null,null,null,null,0.44559285044670105,-0.70667323766601819]
[null,null,20,0.44996261343396809,null,null,null,null,null,null,0.44683584570884705,0.69489500500021018]
[null,null,8,0.58467148402790758,-2.5751783308267345E-4,null,1.2641264638065549E-2,null,0.50002250824067429,null,0.5846714973449707,-2.2777001243789111E-6]
[null,800,14,0.62652671788938785,null,null,null,null,null,null,0.62652671337127686,7.2113620495923274E-7]
[null,null,20,0.64623776341355654,null,null,null,null,null,null,0.64984065294265747,-0.5575176402675307]
[null,null,26,0.65821621215386483,null,null,null,null,null,null,0.65461331605911255,0.54737273683408905]
[null,null,12,0.73156938410319983,-1.6838970558502456E-4,null,1.0188908688201331E-2,null,0.63355059744902742,null,0.73156940937042236,-3.4538381574645515E-6]
[null,1200,18,0.76239268922710346,null,null,null,null,null,null,0.76239269971847534,-1.3761112915439309E-6]
[null,null,24,0.77909335961230308,null,null,null,null,null,null,0.78109192848205566,-0.25652495238146056]
[null,null,30,0.7896656951260842,null,null,null,null,null,null,0.78766709566116333,0.25309437617164782]

{"sheet":"ＦＣＵ能力表","index":2,"n_rows":46,"n_cols":17,"rows_kept":46,"cut":false,"hidden":false,"merged":[[18,15,19,15],[18,1,19,1],[0,9,0,11],[5,9,5,12],[6,9,6,12],[5,2,5,3]]}
[null,"  ＦＣＵ能力表"]
[]
[null,"☆データ入力方法：",null,"水色：必須","橙色：どれか一つ入力",null,"👈　データ入力後、計算実行ボタンを押してください"]
[null,null,"（","黄色：セルに計算式",null,"白色：内部計算）"]
[null,"計算内容："]
[null,1,"１：冷却能力\n２：加熱能力"]
[]
[null,"入口温度"]
[null,"twi ℃"]
[null,7]
[]
[null,"空気状態","乾球温度","湿球温度","相対湿度","露点温度","絶対湿度","エンタルピ","比重"]
[null,null,"DB ℃","WB ℃","RH ％","DP ℃","x kg/kg(DA)","i kJ/kg(DA)","γ kg(DA)/m3"]
[null,"入口 i",26,18.700000762939453,49.563804626464844,14.645060539245605,1.0396827012300491E-2,52.600629219055172,1.1608085632324219]
[null,null,null,"(橙色セルに複数の入力がある場合は、WB→RH→DPの最初の入力値で他の状態値を算出します）"]
[]
[null,"天井吊り隠蔽型－標準型"]
[]
[null,"ユニット\nサイズ","風量","水量","水圧損失",null,"能力",null,null,null,"　　　　水・空気出口状態",null,null,null,"濡れ面係数","対数平均\n温度差","伝熱係数"]
[null,null,null,null,null,"顕熱","全熱","顕熱比","　　　　　　　水側",null,null,"　　　　　　空気側"]
[null,null,"QA","Lw","ΔP","SH","TH","SHF","出入口温度差","出口温度","乾球温度","絶対湿度","エンタルピ","出入口温度差","WSF","MTD","FA・N・K"]
[null,null,"m3/h","L/min","kPa","kW","kW","－","℃","℃","℃","kg/kg'","kJ/kg'","℃","－","℃","kW/℃"]
[null,null,335,2,1.2999999523162842,1.1874986886978149,1.2265092134475708,{"$f":"F23/G23","v":0.96819385918830403},{"$f":"G23*860/(D23*60)","v":8.789982696374258},{"$f":"IF($B$6=1,$B$10+I23,$B$10-I23)","v":15.789982696374258},15.265473365783691,1.0278098285198212E-2,41.310689697265623,{"$f":"IF($B$6=1,$C$14-K23,K23-$C$14)","v":10.734526634216309},{"$f":"1.04*H23^2-2.63*H23+2.59","v":1.0185454732634993},{"$f":"IF($B$6=1,($C$14-J23-K23+$B$10)/LN(($C$14-J23)/(K23-$B$10)),($B$10-K23-J23+$C$14)/LN(($B$10-K23)/(J23-$C$14)))","v":9.2035334668583406},{"$f":"G23/(O23*P23)","v":0.13083857217757885}]
[null,200,335,4,4.4000000953674316,1.3584004640579224,1.6556594371795654,0.82045886584741901,5.9327796498934431,12.932779649893444,13.743958473205566,9.3007907271385193E-3,37.286237226486207,12.256041526794434,1.1322720433908267,9.5595562784222832,0.15296162552909992]
[null,null,335,6,8.8000001907348633,1.4481348991394043,1.87481689453125,0.7724140439333268,4.478729248046875,11.478729248046875,12.942160606384277,8.8200103491544724E-3,35.254032623291018,13.057839393615723,1.179039457931403,9.6012418671785227,0.16561631172113972]
[null,null,335,8,14.399999618530273,1.4851187467575073,1.9634801149368286,0.75637065812876247,3.5179018725951514,10.517901872595152,12.611153602600098,8.6281057447195053E-3,34.432079177856444,13.388846397399902,1.1957256044986173,9.7257577779329036,0.16883851709974923]
[null,null,480,3,3.0999999046325684,1.7085744142532349,1.7735409736633301,0.96336901127471342,8.4735846519470215,15.473584651947021,15.221565246582031,1.0248646140098572E-2,41.191318500518797,10.778434753417969,1.0215425463072996,9.3265726049753734,0.18614985041117429]
[null,300,480,6,10.300000190734863,1.9168519973754883,2.2987604141235352,0.83386332285800224,5.491483211517334,12.491483211517334,13.927727699279785,9.4142351299524307E-3,37.760420562744137,12.072272300720215,1.1200806237395549,9.8546008981964892,0.20825977019738792]
[null,null,480,9,20.899999618530273,2.0201079845428467,2.553128719329834,0.79122841290708645,4.0660938863401057,11.066093886340106,13.284324645996094,9.0223979204893112E-3,36.114070518493655,12.715675354003906,1.160153371501488,9.9928639677360884,0.22022536020144881]
[null,null,480,12,34.299999237060547,2.0596518516540527,2.6491296291351318,0.7774824716019928,3.1642381681336298,10.164238168133629,13.037594795227051,8.8760508224368095E-3,35.492854858398438,12.962405204772949,1.1738792530810365,10.161279658649804,0.22209121438041177]
[null,null,725,4,2.2000000476837158,2.5202505588531494,2.5446133613586426,0.99042573505450537,9.1181978782018032,16.118197878201805,15.469906806945801,1.0397103615105152E-2,41.820729902267459,10.530093193054199,1.0053611789312384,9.1577216875080563,0.27638358841397598]
[null,400,725,8,7.3000001907348633,2.8412041664123535,3.337146520614624,0.85138730015638342,5.979054182767868,12.979054182767868,14.150374412536621,9.5533253625035286E-3,38.339180444717407,11.849625587463379,1.1047061488509904,9.7941686953967722,0.30843306087275835]
[null,null,725,13,17,3.0386269092559814,3.8256070613861084,0.79428620360058999,4.2179770164000683,11.217977016400068,13.336260795593262,9.0534603223204613E-3,36.245501791000365,12.663739204406738,1.1571534806898955,9.9699365272991773,0.33160189286353758]
[null,null,725,18,29.799999237060547,3.1124269962310791,4.0049409866333008,0.77714678109339597,3.1891196745413319,10.189119674541331,13.031418800354004,8.8724019005894661E-3,35.477341632843014,12.968581199645996,1.1742193698627483,10.14765858159125,0.33610969048980055]
[null,null,860,6,5.5999999046325684,3.2213683128356934,3.5884068012237549,0.89771547410318964,8.5723051362567482,15.572305136256748,14.666884422302246,9.8831439390778542E-3,39.700316284179685,11.333115577697754,1.0671370984506985,8.9766425436914066,0.37459978289882712]
[null,600,860,10,13.5,3.5082187652587891,4.3024954795837402,0.81539162142204125,6.1669101874033609,13.16691018740336,13.671009063720703,9.2560965567827225E-3,37.098884887695313,12.328990936279297,1.1369780717967077,9.4184573230750548,0.40178022688099929]
[null,null,860,15,27.200000762939453,3.701240062713623,4.7734737396240234,0.77537664698772313,4.5613193511962891,11.561319351196289,12.999164581298828,8.8534476235508919E-3,35.396589824676511,13.000835418701172,1.1760167209039691,9.6090253720859771,0.42241730446660536]
[null,null,860,20,44.700000762939453,3.7890422344207764,4.9844346046447754,0.76017493155390881,3.5721781333287557,10.572178133328755,12.693116188049316,8.6752753704786301E-3,34.63470521736145,13.306883811950684,1.1917204936387291,9.7648327707093401,0.42832821616058314]
[null,null,1360,8,5.4000000953674316,4.8507418632507324,5.0632929801940918,0.95802116966669948,9.0717332561810817,16.071733256181084,15.200164794921875,1.0234332643449306E-2,41.13324570274353,10.799835205078125,1.0249210677673131,9.0366935552504568,0.54667987000487417]
[null,800,1360,14,14.100000381469727,5.3169279098510742,6.2286567687988281,0.85362351903625966,6.3769581204368952,13.376958120436896,14.17842960357666,9.5710046589374542E-3,38.412502990722658,11.82157039642334,1.1027901816765588,9.6459874956427623,0.58553763492510236]
[null,null,1360,20,26.200000762939453,5.5722928047180176,6.863029956817627,0.81192896428822792,4.9185048023859661,11.918504802385966,13.617327690124512,9.2233121395111084E-3,36.961285850524902,12.382672309875488,1.1402246126941213,9.8840900459969649,0.60896003271566101]
[null,null,1360,26,41.200000762939453,5.7047748565673828,7.1878218650817871,0.79367226451186834,3.9625171820322671,10.962517182032267,13.325850486755371,9.0472223237156868E-3,36.219126113891598,12.674149513244629,1.1577542343273994,10.060766549401913,0.61709191402753949]
[null,null,1690,12,12.100000381469727,6.276301383972168,6.910435676574707,0.90823526586722236,8.2541315025753441,15.254131502575344,14.762228012084961,9.9451383575797081E-3,39.954448148727415,11.237771987915039,1.0592282008607055,9.173320908451247,0.71119600325543797]
[null,1200,1690,18,24.399999618530273,6.6754097938537598,7.9113063812255859,0.84378097272218566,6.2997439702351885,13.299743970235188,14.05766487121582,9.4951782375574112E-3,38.09759169769287,11.94233512878418,1.1113010248657695,9.6042811546248341,0.74122767119049104]
[null,null,1690,24,40.200000762939453,6.9189720153808594,8.5151081085205078,0.81255245702136181,5.0854117870330811,12.085411787033081,13.626921653747559,9.2291748151183128E-3,36.985885051727294,12.373078346252441,1.1396381932617288,9.82433539613519,0.76053637448395972]
[null,null,1690,30,59.099998474121094,7.0644912719726563,8.8721189498901367,0.79625750194209644,4.2389012760586207,11.23890127605862,13.369297981262207,9.0732816606760025E-3,36.329263628005982,12.630702018737793,1.155229819667317,9.9842246820488292,0.76920946485625119]