{"text_format":"1","workbook":"xlsx","n_sheets":1,"sheets":["コイル選定"],"not_rendered":{"charts":4,"images":1,"macros":1,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"コイル選定","index":0,"n_rows":122,"n_cols":40,"rows_kept":122,"cut":false,"hidden":false,"merged":[[0,6,0,7],[0,9,0,11],[4,9,4,12],[5,9,5,12]]}
[null,"  冷温水コイル",null,null,"計算内容：",null,"１：冷水コイル　\n２：温水コイル",null,null,"１：コイル列数計算\n２：出口温度計算"]
[]
[null,"☆データ入力方法：",null,{"$f":"IF(I1=1,\"緑：必須\",\"茶：必須\")","v":"茶：必須"},"青：どれか一つ入力",null,"👈　データ入力後、計算実行ボタンを押してください"]
[null,null,"（","黄：セルに計算式",null,"白：内部計算）",null,null,"（風量基準）"]
[null,"風量","コイル負荷","水量","入口温度","出口温度","出入口温度差",null,null,"１：標準空気(比重1.2kg/m3)の風量を入力"]
[null,"Q m3/h","q kW","L m3/min","twi ℃","two ℃","Δtw ℃",null,null,"　：コイル入口状態の風量を入力　　　　　"]
[null,null,null,null,null,null,{"$f":"IF(F1=1,F7-E7,E7-F7)","v":0},null,null,null,null,null,null,null,"　　標準データ"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"（数値を変更する場合は表の値を書き換えてください：但し、行数、列数は変更しないでください）"]
[null,"空気状態","乾球温度","湿球温度","相対湿度","露点温度","絶対湿度","エンタルピ","比重"]
[null,null,"DB ℃","WB ℃","RH ％","DP ℃","x kg/kg(DA)","i kJ/kg(DA)","γ kg(DA)/m3",null,null,null,null,null,"ユニットサイズ",null,"[","ユニット数",33,"(MAX.33)","]"]
[null,"入口 i",null,null,null,null,null,null,null,null,null,null,null,null,"空調機No.","風量範囲","正面面積","W","EL","チューブ数T","コイル台数"]
[null,"出口 o",null,null,null,null,null,null,null,null,null,null,null,null,null,"m3/h","m2","サイズ","mm","本","台"]
[null,null,null,"(青色セルに複数の入力がある場合は、WB→RH→DPの最初の入力値で他の状態値を算出します）",null,null,null,null,null,null,null,null,null,1,3,2950,0.27400000000000002,21,515,{"$f":"R13*2/3*U13","v":14},1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,2,4,4000,0.372,21,700,{"$f":"R14*2/3*U14","v":14},1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3,5,5680,0.53200000000000003,30,700,20,1]
[null,"・・・☆　計算手順　☆・・・",null,null,null,null,null,null,null,null,null,null,null,4,6,6560,0.61,33,730,22,1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,5,7,7380,0.68400000000000005,36,750,24,1]
[null,"Step1.","コイルの設計面風速",null,null,null,null,null,null,null,null,null,null,6,8,8000,0.748,36,820,24,1]
[null,null,"v0＝",2.5,"m/s",null,null,null,null,null,null,null,null,7,9,9430,0.876,36,960,24,1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,10,10800,1.01,39,1020,26,1]
[null,"Step2.","コイルの必要通過面積",null,null,null,null,null,null,null,null,null,null,9,11,11750,1.1000000000000001,42,1030,28,1]
[null,null,"FAO＝Q/(v0×3600)",null,null,null,null,null,null,null,null,null,null,10,12,12400,1.1499999999999999,45,1010,30,1]
[null,null,"FAD",{"$f":"B7/(D19*3600)","v":0},"m2",null,null,null,null,null,null,null,null,11,13,13500,1.25,48,1030,32,1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,12,14,14650,1.36,48,1120,32,1]
[null,"Step3.","決定通過面積",null,null,null,null,null,null,null,null,null,null,13,15,15950,1.48,48,1220,32,1]
[null,null,"空調機No.",null,{"$f":"IF(I1=1,\"（入力してある場合は、その空調機No.を採用します）\",\"\")","v":""},null,null,null,null,null,null,null,null,14,17,18100,1.68,48,1380,32,1]
[null,null,"FA＝",null,"m2",null,null,null,null,null,null,null,null,15,20,20100,1.87,48,1540,32,1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,16,21,22350,2.08,48,1710,32,1]
[null,"Step4.","実際のコイル通過風速",null,null,null,null,null,null,null,null,null,null,17,22,24100,2.2400000000000002,48,1840,32,1]
[null,null,"va＝Q/(FA×3600)",null,null,null,null,null,null,null,null,null,null,18,25,27200,2.52,51,1950,34,1]
[null,null,"va＝",{"$f":"IFERROR(B7/(D27*3600),\"\")","v":""},"m/s",null,null,null,null,null,null,null,null,19,27,28100,2.61,51,2020,34,1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,20,30,31100,2.89,57,2000,38,1]
[null,"Step5.","ユニットサイズ",null,null,null,null,null,null,null,null,null,null,21,32,33800,3.13,60,2060,40,1]
[null,null,"EL＝",null,"mm",null,null,null,null,null,null,null,null,22,35,36800,3.42,60,2250,40,1]
[null,null,"チューブ数T",null,"(1列当たり)",null,null,null,null,null,null,null,null,23,40,40200,3.72,60,2450,{"$f":"R35*2/3*U35","v":40},1]
[null,null,"台数",null,"台",null,null,null,null,null,null,null,null,24,45,47300,4.3899999999999997,60,2890,40,1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,25,50,52450,4.87,33,2910,44,2]
[null,"Step6.","コイル1本当たりの水速",null,null,null,null,null,null,null,null,null,null,26,55,57750,5.36,36,2940,48,2]
[null,null,"コイル内径di",{"$f":"0.01588-0.00045*2","v":1.4979999999999999E-2},"m",null,null,null,null,null,null,null,null,27,60,63050,5.85,39,2960,52,2]
[null,null,"コイル断面積S",{"$f":"D39^2*3.14/4","v":1.7615431399999997E-4},"m2",null,null,null,null,null,null,null,null,28,65,68250,6.32,39,3200,52,2]
[null,null,"水速vw＝L/(T×S×60)",null,null,null,null,null,null,null,null,null,null,29,70,73500,6.82,39,3450,52,2]
[null,null,"vw＝",{"$f":"IFERROR(D7/(D35*D40*60),\"\")","v":""},"m/s",null,null,null,null,null,null,null,null,30,75,78800,7.3,42,3430,56,2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,31,80,84000,7.79,42,3660,56,2]
[null,"Step7.","フローの決定",null,null,"水速",null,null,null,null,null,null,null,32,90,94500,8.76,45,3840,60,2]
[null,null,"HF：","     vw≦1.01",null,"→vc＝2vw",null,null,null,null,null,null,null,33,100,105000,9.73,48,4000,64,2]
[null,null,"SF：","1.01<vw≦2.01",null,"→vc＝vw"]
[null,null,"DF：","2.01<vw≦4.02",null,"→vc＝vw/2"]
[null,null,"TF：","4.02<vw≦6.03",null,"→Vw＝vc/3",null,null,null,null,null,null,null,null,"K：冷却時の伝熱係数(７フィン型コイル)",null,null,null,"W/m2K列",null,null,null,null,null,null,null,null,"K：加熱時の伝熱係数(７フィン型コイル)",null,null,null,"W/m2K列"]
[null,null,"フロー",null,{"$f":"IF(I1=1,\"（入力してある場合は、そのフロー型式を採用します）\",\"\")","v":""},null,null,null,null,null,null,null,null,null,"コイル正面風速",null,null,null,null,null,"水速","m/s",null,null,null,null,null,"コイル正面風速",null,null,null,null,null,"水速","m/s"]
[null,null,"vc＝",null,"m/s",null,null,null,null,null,null,null,null,null,"m/s",0.1,0.2,0.30000000000000004,0.4,0.5,0.7,0.89999999999999991,1.0999999999999999,1.3,1.5000000000000002,2,null,"m/s",0.1,0.2,0.30000000000000004,0.4,0.5,0.7,0.89999999999999991,1.0999999999999999,1.3,1.5000000000000002,2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,0,29.069767441860467,31.395348837209301,34.883720930232556,37.209302325581397,38.372093023255815,40.697674418604649,43.02325581395349,44.186046511627907,45.348837209302324,46.511627906976742,46.511627906976742,null,0,29.069767441860467,31.395348837209301,34.883720930232556,37.209302325581397,38.372093023255815,40.697674418604649,43.02325581395349,44.186046511627907,45.348837209302324,46.511627906976742,46.511627906976742]
[null,"Step8.","7フィン型コイルの伝熱係数",null,null,null,null,null,null,null,null,null,null,2,{"$f":"O51+0.2","v":0.2},145.34883720930233,151.16279069767441,174.41860465116278,209.30232558139537,216.27906976744185,223.25581395348837,229.06976744186048,233.72093023255815,236.04651162790699,238.37209302325581,239.53488372093022,null,{"$f":"AB51+0.2","v":0.2},145.34883720930233,151.16279069767441,174.41860465116278,209.30232558139537,216.27906976744185,223.25581395348837,229.06976744186048,233.72093023255815,236.04651162790699,238.37209302325581,239.53488372093022]
[null,null,"K＝",null,"W/m2K列",null,null,null,null,null,null,null,null,3,0.4,199.44441712965238,227.78078240490356,256.11714768015469,283.3636527525116,330,344,351.99999999999994,357,362,366,370,null,0.4,199.44441712965238,227.78078240490356,256.11714768015469,283.3636527525116,330,344,351.99999999999994,357,362,366,370]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,0.60000000000000009,241.86046511627907,289.26314817501878,322.00991966653032,354.75669115804186,410.00000000000006,425.75,434.75,440.37499999999994,446,450.5,455,null,0.60000000000000009,241.86046511627907,289.26314817501878,322.00991966653032,354.75669115804186,410.00000000000006,427.5,437.5,443.74999999999994,450,455,460]
[null,"Step9.","濡れ面係数",null,null,null,null,null,null,null,null,null,null,5,0.8,284.37815975733065,352.62891809909007,392.44186046511635,426.56723963599603,459.99999999999994,482.75000000000006,495.75,503.875,512,518.5,525,null,0.8,296.7424275728668,367.96061019035494,409.50455005055625,445.11364135930029,480,499.25000000000006,510.25,517.125,524,529.5,535]
[null,null,"SHF",null,"－",null,null,null,null,null,null,null,null,6,1,311.17581269329531,391.51574978865511,429.98839572164439,467.3294932448398,515,537.75,550.75,558.875,567,573.5,580,null,1,323.26031027361745,406.72024492607864,446.68697419627136,485.47821142910539,535,554.25,565.25,572.125,579,584.5,590]
[null,null,"WSF",null,"－",null,null,null,null,null,null,null,null,7,1.2,336.33958458187772,427.55031938374287,470.87541841462877,513.06038326049145,555,584.75,601.75,612.37500000000011,623,631.5,640,null,1.2,351.49001631980013,446.80934277940696,492.08602284772013,536.17121133528838,580,604.5,618.5,627.25000000000011,636,643,650]
[null,null,null,null,null,null,null,null,null,null,null,null,null,8,1.4,358.24400345763246,459.93907540689588,511.94223719913288,552.38914081531721,585,620.00000000000011,640,652.5,665,675,685,null,1.4,376.61549081443411,483.52569465853156,538.19568526062687,580.71678906225657,615,641.25000000000011,656.25,665.625,675,682.5,690]
[null,null,null,null,null,null,null,null,null,null,null,null,null,9,1.5999999999999999,373.78147713332197,481.73699692648631,542.09922304739541,586.21008059729058,615,655,677.5,692.5,705,715,730,null,1.5999999999999999,395.05359371814518,509.15292358083917,572.95039834277566,619.57162989957544,650,679.56521739130437,696.195652173913,707.28260869565213,716.52173913043475,723.91304347826087,735]
[null,"Step10.","対数平均温度差",null,null,null,null,null,null,null,null,null,null,10,1.7999999999999998,382.77552081368094,498.06935238406675,559.1750831163713,605.29261574452562,645.00000000000011,680,707.50000000000011,722.5,736.66666666666663,750,765,null,1.7999999999999998,403.5462855089969,525.09637150568267,589.51791708392625,638.13795148260056,680,707.70833333333326,729.47916666666674,741.35416666666663,752.56944444444434,763.125,775]
[null,null,"MTD=(Δt1-Δt2)/loge(Δt1/Δt2)",null,null,null,null,null,null,null,null,null,null,11,1.9999999999999998,391.78095461039845,512.77213176949215,581.90994728897431,628.0018243019623,670.00000000000011,710,732.50000000000011,752.5,766.66666666666663,780,800,null,1.9999999999999998,412.24712388109083,539.5587356678983,612.30822811750272,660.80788975057214,705,737.30769230769226,755.48076923076928,771.63461538461536,783.07692307692298,793.84615384615381,810]
[null,null,"DBi－two",null,"Δt1℃",null,null,null,null,null,null,null,null,12,2.1999999999999997,400.02037921007047,529.50674473471759,601.18669707871868,650.90021241407419,690,740,762.5,785,801.66666666666663,815,835,null,2.1999999999999997,423.20996641065426,560.20278790774466,636.03809980791982,688.63355806126697,730,767.93103448275861,785,802.06896551724139,814.71264367816093,824.82758620689651,840]
[null,null,"DBo－twi",null,"Δt2℃",null,null,null,null,null,null,null,null,13,2.4,404.70940633190497,538.07955160037363,613.96256528760591,664.55124107909398,715,760,787.5,810,826.66666666666663,840,865,null,2.4,427.35049200082278,568.18190413745754,648.31012138761196,701.72893288771468,755,791,813,831,844.33333333333326,855,875]
[null,null,"MTD",{"$f":"IF(D62=D63,D62,(D62-D63)/LN(D62/D63))","v":0},"℃",null,null,null,null,null,null,null,null,14,2.6,413.09630529645796,552.71824088548419,628.8756602976805,683.10897412151712,730,780,810,832.50000000000011,853.33333333333337,869.99999999999989,890,null,2.6,438.56114603391086,586.78991326883602,667.64196812424984,725.21843143037779,775,814.0625,837.5,855.07812500000011,871.35416666666674,884.37499999999989,900]
[null,null,null,null,null,null,null,null,null,null,null,null,null,15,2.8000000000000003,417.51216873985936,558.98323418063819,641.79556517036235,697.00378583017846,750,800,832.50000000000011,857.49999999999989,876.66666666666663,890,915,null,2.8000000000000003,445.34631332251666,596.24878312601402,684.58193618171981,743.47070488552367,800,839.39393939393938,865.00000000000011,884.69696969696963,899.79797979797979,910.30303030303025,930]
[null,"Step11.","コイル決定列数",null,null,null,null,null,null,null,null,null,null,16,3.0000000000000004,424.0695376762568,570.41962268953023,654.54211250030937,714.46498195456309,765,820.00000000000011,852.5,877.5,898.33333333333337,915,940,null,3.0000000000000004,451.78650092307095,607.70195096989164,697.32264272908776,761.1620395986522,815,857.42857142857156,882.5,901.78571428571433,917.85714285714289,930.71428571428567,950]
[null,null,"N=q/(FA×K/1000×WSF×MTD)",null,null,null,null,null,null,null,null,null,null,17,3.2000000000000006,427.6653353857248,576.36837653062639,666.28184326940413,726.22415442858937,780,835,872.5,900,923.33333333333337,940,965,null,3.2000000000000006,457.82122441933359,617.00973641419614,713.26325529481085,777.43226788188736,835,876.62162162162167,905,925.81081081081084,943.46846846846847,956.08108108108104,975]
[null,null,"計算列数",{"$f":"IFERROR(C7*1000/(D27*D53*D57*D64),\"\")","v":""},"列",null,null,null,null,null,null,null,null,18,3.4000000000000008,431.77342163535616,584.90906184202913,673.56653775115558,736.89330625767457,795.00000000000011,855,890,917.5,940,960,990,null,3.4000000000000008,461.64453885541212,625.37446863613161,720.16548061444291,787.87334631323677,850,896.15384615384608,923.07692307692298,944.23076923076917,961.53846153846155,976.92307692307691,1000]
[null,null,"安全率",5,"％",null,null,null,null,null,null,null,null,19,3.600000000000001,433.72093023255815,590.58450013020047,682.32578170382396,745.39791278568998,810,865,905,935,960,980,1010,null,3.600000000000001,463.17111685328746,630.68591680570796,728.65654465902196,796.01135130817511,865,907.625,938.625,961.875,981.25,996.75,1020]
[null,null,"N=",null,"列",null,null,null,null,null,null,null,null,20,3.8000000000000012,438.60227677452542,600.19258927040312,695.9925602501022,759.47446873062563,820.00000000000011,880,922.5,955,980,1000,1030,null,3.8000000000000012,470.69512629461258,644.10912019262764,746.91884514645108,815.04577132067129,880,925.71428571428567,958.09523809523807,982.85714285714278,1001.9047619047619,1017.1428571428571,1040]
[null,null,null,null,null,null,null,null,null,null,null,null,null,21,4.0000000000000009,442,607.21523193911389,705.52626949116097,769.13929378954435,830,894.99999999999989,937.5,969.99999999999989,994.99999999999989,1015,1045,null,4.0000000000000009,473.95180722891564,651.11030894676071,756.52816849052203,824.73972466589692,890,941.39534883720921,975,1000.6976744186046,1020.4651162790697,1036.2790697674418,1060]
[null,"Step12.","コイルの空気側圧力損失（コイルの空気側圧力損失表）",null,null,null,null,null,null,null,null,null,null,22,4.2000000000000011,446.18712817739322,614.23163099745034,715.0583326894847,776,842,910,952.5,985,1010,1030,1065,null,4.2000000000000011,480,660,765,840,905,959.44444444444446,992.5,1017.7777777777778,1037.2222222222222,1052.7777777777778,1080]
[null,null,"ΔPa＝",null,"Pa",null,null,null,null,null,null,null,null,23,4.4000000000000012,446.51162790697674,615.07089338634125,715.0917676379521,781.77235047235911,855,919.99999999999989,965,1000,1025,1045,1085,null,4.4000000000000012,481.19386496120865,663.96073610013514,772.1208587834908,845.49071562387576,915,965.86956521739125,1001.0869565217391,1028.4782608695652,1048.0434782608695,1063.695652173913,1095]
[null,null,null,null,null,null,null,null,null,null,null,null,null,24,4.6000000000000014,448.67245847622678,621.23878865939105,724.7785867692894,791.50423444011301,865,935,980,1015,1040,1060,1100,null,4.6000000000000014,486,667.92147220027016,779.24171756698172,850.98143124775163,930,983.61702127659578,1018.0851063829787,1044.8936170212767,1064.0425531914893,1079.3617021276596,1110]
[null,"Step13.","コイルの水側圧力損失",null,null,null,null,null,null,null,null,null,null,25,4.8000000000000016,451.27095727420232,627.40477478173534,731.01290272734309,800.08498802441477,875,944.99999999999989,992.5,1027.5,1051.6666666666667,1075,1115,null,4.8000000000000016,487,674.01198662266427,785.31671835851716,859.51987284908557,940,993.95833333333326,1030.5729166666667,1057.5520833333333,1076.1805555555557,1094.1666666666667,1125]
[null,null,"チューブ相当長CＬ",null,null,null,null,null,null,null,null,null,null,26,5.0000000000000018,456.38920300899753,635.47863710113575,739.466050444958,814.56807119327402,880,955,1002.5,1040,1066.6666666666667,1090,1130,null,5.0000000000000018,492.692889611986,686.02807414327162,798.28721354853428,879.36325867455719,950,1007,1043.0999999999999,1071.5999999999999,1091.8666666666668,1109.5999999999999,1140]
[null,null,"CL=EL×N/(KS×1000)+0.11×(N/KS+1)",null,null,null,null,null,null,null,null,null,null,null,"註）カタログの水速範囲が0.5～2m/sのため、0.4m/s以下の数値は想定した。",null,null,null,null,null,null,null,null,null,null,null,null,"註）カタログの水速範囲が0.5～2m/sのため、0.4m/s以下の数値は想定した。"]
[null,null,"KS＝",{"$f":"IF(D49=\"\",\"\",IF(D49=\"HF\",0.5,IF(D49=\"SF\",1,IF(D49=\"DF\",2,3))))","v":""},"(HF：0.5 SF：1 DF：2 TF：3)"]
[null,null,"CL＝",{"$f":"IFERROR(D34*D70/(D78*1000)+0.11*(D70/D78+1),\"\")","v":""}]
[null,null,"ΔPw＝1.1956×vc1.73×CL",null,null,null,null,null,null,null,null,null,null,null,"WSF：濡れ面係数",null,null,null,null,"NC：コイル決定列数",null,null,null,null,null,null,null,"Pa：コイルの空気側圧力圧損(７フィン濡れ面時)",null,null,null,null,"Pa"]
[null,null,"ΔPw＝",{"$f":"IFERROR(0.122*D50^1.73*D79*9.8,\"\")","v":""},"kPa",null,null,null,null,null,null,null,null,null,"顕熱比","WSF",null,null,null,"計算列数",null,"コイルフロー型式",null,null,null,null,null,"コイル正面風速",null,null,null,null,"コイル列数"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"SHF",null,null,null,null,"列","HF","SF","DF","TF",null,null,null,"m/s",1,2,3,4,5,6,7,8,9,10,11,12]
[null,"Step14.","コイルの仕様",null,null,null,null,null,null,null,null,null,null,null,0.38,1.74,null,null,null,1,1,null,null,null,null,null,null,0,0,0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.4,1.7050000000000001,null,null,null,2,2,2,2,null,null,null,null,1,4.5914999999999999,9.8000000000000007,13.72,19.600000000000001,23.52,29.400000000000002,33.107100000000003,37.24,41.983499999999999,46.06,50.545500000000004,54.88]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.45,1.615,null,null,null,3,3,null,null,3,null,null,null,2,12.474299999999999,26.460000000000004,41.160000000000004,52.920000000000009,66.64,80.36,94.215900000000005,107.80000000000001,120.6823,135.24,146.75829999999999,158.76]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.5,1.53,null,null,null,4,4,4,4,null,null,null,null,3,23.976900000000001,50.960000000000008,76.44,100.94000000000001,127.4,154.84000000000003,179.66130000000001,204.82,230.75289999999998,257.74,281.44289999999995,305.76]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.55000000000000004,1.4550000000000001,null,null,null,5,5,null,null,null,null,null,null,4,41.805,82.320000000000007,123.48,161.70000000000002,204.82,245.00000000000003,285.3066,328.3,366.59699999999998,403.76000000000005,447.94899999999996,490.00000000000006]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.6,1.385,null,null,null,6,6,6,6,6,null,null,null,5,65.824799999999996,117.60000000000001,174.44000000000003,235.20000000000002,291.06,344.96000000000004,409.72919999999999,464.52000000000004,536.61680000000013]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.65,1.3149999999999999,null,null,null,7,7,null,null,null,null,null,null,"註）空気側圧力損失はメーカ、入口空気条件等によって変わるため、実際の値はメーカに再確認する。"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.7,1.2549999999999999,null,null,null,8,8,8,8]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.75,1.1950000000000001,null,null,null,9,9,null,null,9,null,null,null,"y=ax2+bx",null,"x：列数","で数式化"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.8,1.145,null,null,null,10,10,10,10,null,null,null,null,"a=",{"$f":"(AC86*$AB85-AC85*$AB86)/($AB86^2*$AB85-$AB85^2*$AB86)","v":1.7551500000000004},{"$f":"(AD86*$AB85-AD85*$AB86)/($AB86^2*$AB85-$AB85^2*$AB86)","v":3.7566666666666677},{"$f":"(AE86*$AB85-AE85*$AB86)/($AB86^2*$AB85-$AB85^2*$AB86)","v":4.8999999999999959},7.1866666666666674,9.1466666666666665,11.433333333333346,12.779150000000007,14.373333333333326,16.576483333333329,18.293333333333333,20.435149999999982,22.540000000000003]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.85,1.095,null,null,null,11,11,null,null,null,null,null,null,"b=",{"$f":"(AC86-AC$92*$AB86^2)/$AB86","v":2.7268499999999989},{"$f":"(AD86-AD$92*$AB86^2)/$AB86","v":5.7166666666666659},{"$f":"(AE86-AE$92*$AB86^2)/$AB86","v":10.78000000000001},12.086666666666668,15.026666666666671,17.313333333333304,21.549649999999986,25.153333333333354,27.188183333333342,31.033333333333342,32.508850000000031,34.29999999999999]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.9,1.0549999999999999,null,null,null,12,12,12,12,12,null,null,null,"コイル正面風速",null,null,null,null,"コイル列数"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.95,1.0249999999999999,null,null,null,null,null,null,null,null,null,null,null,"m/s",1,2,3,4,5,6,7,8,9,10,11,12]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,1,null,null,null,null,null,null,null,null,null,null,null,0,{"$f":"AC$92*$AB96^2+AC$93*$AB96","v":0},0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"      SHF＝ｑｓ／ｑｔ",null,null,null,null,null,null,null,null,null,null,null,null,1,4.4819999999999993,9.4733333333333327,15.680000000000007,19.273333333333333,24.173333333333339,28.746666666666648,34.328799999999994,39.526666666666678,43.76466666666667,49.326666666666675,52.944000000000017,56.839999999999989]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,12.474299999999999,26.46,41.160000000000004,52.92,66.640000000000015,80.359999999999985,94.215900000000005,107.80000000000001,120.6823,135.24,146.75829999999999,158.76]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3,23.976900000000001,50.960000000000008,76.44,100.94000000000001,127.4,154.84000000000003,179.66130000000001,204.82,230.75289999999998,257.74,281.44289999999995,305.76]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"WSF＝",1.04,"×SHF２＋",-2.63,"×SHF＋",2.59,null,null,null,null,null,null,null,4,38.989800000000002,82.973333333333343,121.51999999999998,163.33333333333334,206.45333333333335,252.18666666666675,290.66500000000008,330.58666666666664,373.97646666666662,416.82666666666671,456.99779999999987,497.84000000000003]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5,57.513000000000005,122.50000000000001,176.39999999999995,240.10000000000002,303.8,372.4000000000002,427.22700000000009,485.09999999999991,550.35299999999995,612.5,673.42299999999977,735]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"註）メーカで使用している係数に合わせた。"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"※７フィン乾き面時の圧力損失は上記の値／1.35とした。"]